## 11 KV June 2025
Sl No | Town Name | Substation | Feeder Name | Feeder Code | Rural/Urban | No_of_Consumers | No_of_Outages | Duration_of_Outage_Sec | Average_Hours_of_Steady_Supply | Reason for power disruptions
1 | MAPUSA | 220/33KV Thivim | 11KV Thivim Village | 1S03-1105 | RURAL | 3173 | 9 | 21960 | 23:48 | 1)Trip on O/C E/F pulled incomer II 2)Manually trip as per request of HT staff Nachinola Vijay to remove mango tree branch fallen on line 3)Trip on O/C, D/F informed to Nachinola S/S S.O Sunil charge after opening ground ABS by L/W Vishal Nachinola S/S HT staff stood ok. 4)Manually trip to open compound ABS to close ground ABS stood ok. 5)Manually trip to open lala tapping ABS & to close compound ABS stood ok supply up to lala tapping (fault tree fallen on on line) 6)Manually trip to close lala tapping ABS after attending tree fallen on line stood ok full feeder charged. 7)Manually trip requested by Saideep to close comprem ABS to feed supply upto Fucat vaddo 8)Manually trip LC issued to Nachinola S/S S.O Khambal to attend mouth ABS at coprem charge after attending mouth ABS & LC return. 9)Manually trip as per request of L/W Sandeep to attend L/T conductor, L/T HT combine.
2 | MAPUSA | 33KV Bicholim | 11KV MAYEM | 1S05-1107 | RURAL | 756 | 30 | 57300 | 23:28 | planned shutdown, O/C, E/F, falling of trees/branches due to heavy rain and wind, Change over of supply,
3 | MAPUSA | 33KV Sanquelim | 11KV Sanquelim | 1S08-1102 | URBAN | 1599 | 0 | 0 | 24:00:00
4 | MAPUSA | 33KV Porvorim | 11KV Porvorim Bazar | 1S09-1109 | RURAL | 1849 | 5 | 4260 | 23:58 | E/f, Guarding snapped, Jumper opened etc.
5 | MAPUSA | 33KV Porvorim | Audit bhavan | 1S09-1112 | URBAN |  | 0 | 0 | 24:00:00
6 | MAPUSA | 33KV Valpoi | 11KV Bhironda | 1S11-1101 | RURAL | 2606 | 41 | 89820 | 23:10 | Due to heavy rain , trees fallen on line, isolation of faulty section,O/c & E/F , 33KV line failure at Valpoi SS
7 | MAPUSA | 33KV Candolim | 11KV Candolim | 1S12-1103 | RURAL | 2097 | 0 | 0 | 24:00:00
8 | PANJIM | 33KV Nagali hills(IT Park) | 11KV BSNL | 2S07-1105 | URBAN |  | 0 | 0 | 24:00:00
9 | PANJIM | 33KV Madkai | 11KV Industry I | 2S15-1104 | URBAN | 31 | 7 | 12180 | 23:53 | Mannual trip - attending broken AB switch on 33 KV BUS -II and and Red hot attending on 6.3 MVR transformer -II,
10 | MARMAGAO | 33KV Bogda | HEADLAND | 3S06-1101 | URBAN |  | 0 | 0 | 24:00:00
11 | MARGAO | 33KV Monte Hill | 11KV Hari Mandir | 4S03-1105 | URBAN | 4581 | 4 | 4684.2 | 23:57 | RMU problem at Chaitanya.
12 | MARGAO | 33KV Aquem | 11KV Khareband | 4S04-1101 | URBAN | 5182 | 0 | 0 | 24:00:00
13 | MARGAO | 33KV Carmona | 11KV Zalor | 4S08-1101 | RURAL | 546 | 18 | 18182.4 | 23:50 | 33KV Velim-II incoming supply failure
14 | MARGAO | 33KV Cuncolim | 11KV Dharmapur | 4S09-1106 | RURAL | 3011 | 0 | 0 | 24:00:00
15 | MARGAO | 33KV Pontemol | 11KV Bansai | 4S13-1105 | RURAL | 4480 | 11 | 16800 | 23:51 | To attend red hot on 11KV Bay at Pontemol substation, Alternate supply were given on Bansai feeder. Also power interruption occurred during breaker servicing work.
16 | MAPUSA | 33KV Mapusa | 11KV Althino | 1S04-1105 | URBAN | 6119 | 0 | 0 | 24:00:00
17 | MAPUSA | 33KV Mapusa | 11KV Siolim | 1S04-1112 | RURAL | 3827 | 0 | 0 | 24:00:00
18 | MAPUSA | 33KV Nachinola | 11KV Aldona UG | 1S06-1105 | RURAL |  | 6 | 6960 | 23:56 | Cable fault.
19 | MAPUSA | 33KV Nagoa | 11KV AGARWADDO | 1S07-1109 | RURAL |  | 27 | 19549.8 | 23:49 | Cable fault,RMU fleash over, Jumper cut on 33Kv Mapusa-III Ckt
20 | MAPUSA | 33KV Saligao | 11KV Betim | 1S10-1105 | RURAL | 3218 | 0 | 0 | 24:00:00
21 | MAPUSA | 33 KV Anjuna | 11KV Starco | 1S15-1103 | RURAL |  | 8 | 12180 | 23:53 | 1)Trip on O/C, E/F after conferming HT staff Vijay test charge taken both feeder holding. 2)Trip on E/F informed HT staff L/W Vishal after conferming, test charged Feeder holding. 3)Trip on E/F informed HT staff and take test charged stood ok. 4)Trip of E/F informed HT staff and take test charged stood ok 5)Trip on E/F informed HT staff after open LAFranza transformer by LT staff take test charged stood ok after charged Lafranza transformer stood ok full feeder charged. 6)Trip on E/F informed LT staff to open Matta RMU and Rohan J.E after open Lafranza transformer feeder charge stood ok. 7)D/F on O/C. as per instructions of J.E Manoj HT staff L/W Sandesh taken test charge after opening Anjuna side isolator, stood ok. Same informed L/W Sandeep HT staff. 8)Tripped on O/C , E/F.after conferming HT staff took test charge taken,. Feeder stood ok.no fault found
22 | PANJIM | 33KV Corlim | 11KV New Ind.Estate | 2S01-1103 | URBAN | 327 | 13 | 12660 | 23:53 | Tripped on Earth fault and Over current , found post insulator faulty on Ravalnath Nagar on double pole structure, same is isolated and feeder charge stood ok.
23 | PANJIM | 33KV EDC | 11KV Patto- Plaza | 2S02-1103 | URBAN | 515 | 0 | 0 | 24:00:00
24 | PANJIM | 33KV Bambolim | 11KV Siridao | 2S05-1101 | RURAL | 1053 | 0 | 0 | 24:00:00
25 | PANJIM | 33KV Nagali hills(IT Park) | 11KV Adraar | 2S07-1101 | URBAN | 1327 | 0 | 0 | 24:00:00
26 | PANJIM | 33KV Nagali hills(IT Park) | 11KV CARANZALEM | 2S07-1102 | URBAN | 957 | 0 | 0 | 24:00:00
27 | PANJIM | 33KV Curti | 11KV Shanti Nagar | 2S10-1105 | URBAN | 4256 | 0 | 0 | 24:00:00
28 | PANJIM | 33KV Kundaim | 11KV Mardol | 2S14-1101 | RURAL | 3618 | 16 | 83400 | 23:14 | 1. Manually tripped to attend faults 2. To attend cut jumper 3. Overcurrent & Earth fault
29 | MARMAGAO | 110/33/11 KV Verna | 11KV IFB | 3S04-1104 | URBAN | 120 | 0 | 0 | 24:00:00
30 | MARGAO | 33KV Benaulim | 11KV Colva | 4S07-1102 | RURAL | 4699 | 0 | 0 | 24:00:00
31 | MARGAO | 33KV Velim | 11KV Dramapur | 4S10-1105 | RURAL |  | 0 | 0 | 24:00:00
32 | MARGAO | 33KV Canacona | 11KV Agonda | 4S11-1101 | RURAL | 1432 | 0 | 0 | 24:00:00
33 | MARGAO | 33KV Canacona | 11KV Gaondongri | 4S11-1104 | RURAL | 2395 | 6 | 50460 | 23:32 | Incoming supply failure and load changeover.
34 | MARGAO | 33KV Pontemol | 11KV Kakoda | 4S13-1108 | URBAN | 1568 | 11 | 18180 | 23:50 | To replace failed LA, Alternate supply were given on Kakoda feeder. Also power interruption occurred during breaker servicing work.
35 | MARGAO | 33KV Shigao | 11KV Dhat | 4S14-1103 | RURAL | 861 | 0 | 0 | 24:00:00
36 | MARGAO | 33KV Xelpem | 11KV Ponsamol | 4S18-1102 | RURAL | 1555 | 0 | 0 | 24:00:00
37 | MAPUSA | 33KV Pernem | 11KV Sawal | 1S01-1104 | RURAL | 453 | 20 | 28380 | 23:44 | M.T to to attend burnt fuse at Kadamba Bus stand, Changeover of supply
38 | MAPUSA | 33KV Tuem | 11KV Industry | 1S02-1101 | URBAN |  | 10 | 62100 | 23:26 | M.T for changeover of supply.
39 | MAPUSA | 220/33KV Thivim | 11KV Colvale | 1S03-1104 | RURAL | 3897 | 0 | 0 | 24:00:00
40 | MAPUSA | 33KV Mapusa | 11KV Duler | 1S04-1102 | URBAN | 7977 | 1 | 420 | 24:00 | Change over at Substation
41 | MAPUSA | 33KV Mapusa | 11KV City | 1S04-1103 | RURAL | 3601 | 0 | 0 | 24:00:00
42 | MAPUSA | 33KV Sanquelim | 11KV Poriem | 1S08-1101 | RURAL | 3862 | 0 | 0 | 24:00:00
43 | MAPUSA | 33KV Valpoi | 11KV Saleli | 1S11-1102 | RURAL | 3024 | 23 | 49260 | 23:33 | Due to heavy rain , trees fallen on line, isolation of faulty section,O/c & E/F , 33KV line failure at Valpoi SS
44 | MAPUSA | 33KV Candolim | 11KV Highland | 1S12-1106 | RURAL | 2331 | 0 | 0 | 24:00:00
45 | MAPUSA | 33 KV Anjuna | 11KV vagator | 1S15-1102 | RURAL |  | 0 | 0 | 24:00:00
46 | PANJIM | 33KV EDC | 11KV Old bus stand | 2S02-1101 | URBAN | 915 | 0 | 0 | 24:00:00
47 | PANJIM | 33KV Curti | 11KV Durbhat | 2S10-1106 | RURAL | 2896 | 0 | 0 | 24:00:00
48 | PANJIM | 33KV Madkai | 11KV Karanzal | 2S15-1103 | RURAL | 697 | 3 | 22740 | 23:47 | Over current / Earth fault relay - line pulled by Incomer -I, and 33 KV in Madkai yard 6.3 MVA Transformer Fuse Burnt , Test charge taken found OK
49 | MARMAGAO | 33KV Sancoale | 11KV Cansualim | 3S03-1102 | RURAL | 2789 | 10 | 13620 | 23:52 | On 2/6/2025, 00:45 to 01:20 = 35 mins, due to failure of 11KV disc insulator, on 11/6/25 from 23:20 to 00:30 = 70 mins coconut palm had fallen on line, on 23/6/24, from 11:12 to 12:30 = 78 mins conductor had snapped at Velsao, on 24/06/2025 from 10:15 to 11:05 = 50mins shutdown was availed by Majorda staff.
50 | MARMAGAO | 110/33/11 KV Verna | 11KV Verna | 3S04-1101 | RURAL | 3069 | 0 | 0 | 24:00:00
51 | MARMAGAO | 110/33/11 KV Verna | 11KV Nagoa | 3S04-1106 | RURAL | 1407 | 6 | 6720 | 23:56 | Over Current and Earth Fault
52 | MARGAO | 33KV Raia | 11KV Curtorim | 4S01-1105 | RURAL | 3128 | 0 | 0 | 24:00:00
53 | MARGAO | 33KV Fatorda | 11KV Ambaji | 4S02-1101 | URBAN | 3412 | 0 | 0 | 24:00:00
54 | MARGAO | 33KV Monte Hill | 11KV Mutt | 4S03-1106 | URBAN | 578 | 0 | 0 | 24:00:00
55 | MARGAO | 33KV Aquem | 11KV Margao I | 4S04-1107 | URBAN |  | 9 | 10020 | 23:54 | OCR - Due Tr. Side found moisture
56 | MARGAO | 33KV Nessai | 11KV Goa Carbon | 4S06-1104 | URBAN | 2445 | 0 | 0 | 24:00:00
57 | MARGAO | 33KV Carmona | 11KV Janoth Bazar | 4S08-1102 | URBAN | 1416 | 0 | 0 | 24:00:00
58 | MARGAO | 33KV Cuncolim | 11KV Cuncolim | 4S09-1105 | RURAL | 3243 | 0 | 0 | 24:00:00
59 | MARGAO | 33KV Pontemol | 11KV Panchwadi | 4S13-1102 | RURAL | 3115 | 0 | 0 | 24:00:00
60 | MARGAO | 33KV Xelpem | 11KV Malkarne | 4S18-1104 | RURAL | 996 | 0 | 0 | 24:00:00
61 | MAPUSA | 33KV Pernem | 11KV Keri | 1S01-1106 | RURAL | 6288 | 20 | 42720 | 23:36 | Tree branch fallen on line at Parashte, Coconut leaf fallen on line at Kaloba Temple parashte, Coconut tree fallen on line at Konadi, tree cutting at substation yard, Conductor snapped at Balkhajan Korgao.
62 | MAPUSA | 33KV Tuem | 11KV Mandrem | 1S02-1102 | RURAL | 5315 | 9 | 11400 | 23:54 | 11KV Mandrem OH feeder is interlinked with 11KV Tuem OH feeder at Tuem S/S and power interruption of 11KV line in V.P. Tuem has caused more power interruption of Mandrem feeder
63 | MAPUSA | 33KV Mapusa | 11KV Industry | 1S04-1101 | URBAN | 56 | 0 | 0 | 24:00:00
64 | MAPUSA | 33KV Mapusa | 11KV Karaswada | 1S04-1104 | URBAN | 1148 | 0 | 0 | 24:00:00
65 | MAPUSA | 33KV Mapusa | 11KV Parra | 1S04-1113 | RURAL | 3764 | 0 | 0 | 24:00:00
66 | MAPUSA | 33KV Bicholim | 11KV Lamgao | 1S05-1112 | RURAL |  | 9 | 30000 | 23:43 | O/C, E/F , planned shutdown for LT tree cutting
67 | MAPUSA | 33KV Nachinola | 11KV Pomburpa | 1S06-1101 | RURAL | 1451 | 0 | 0 | 24:00:00
68 | MAPUSA | 33KV Porvorim | 11KV Malim | 1S09-1104 | RURAL | 1570 | 0 | 0 | 24:00:00
69 | PANJIM | 33KV EDC | 11KV BAL BHARTI | 2S02-1108 | URBAN |  | 0 | 0 | 24:00:00
70 | MARMAGAO | 33KV Kadamba | 11KV Waddem Lake | 3S02-1104 | URBAN | 2330 | 17 | 32700 | 23:42 | m/t, incoming supply failed mean time shutdown taken to work on new vaddem feeder.
71 | MARMAGAO | 33KV Sancoale | 11KV Sesa Goa | 3S03-1101 | URBAN | 1484 | 0 | 0 | 24:00:00
72 | MARMAGAO | 110/33/11 KV Verna | 11KV SMARTLINK | 3S04-1109 | URBAN |  | 0 | 0 | 24:00:00
73 | MARGAO | 33KV Fatorda | 11KV Gogol | 4S02-1106 | RURAL |  | 0 | 0 | 24:00:00
74 | MARGAO | 33KV Aquem | 11KV Davorlim | 4S04-1106 | RURAL | 2293 | 0 | 0 | 24:00:00
75 | MARGAO | 33KV Nessai | 11KV Chandor | 4S06-1103 | RURAL | 2911 | 0 | 0 | 24:00:00
76 | MARGAO | 33KV Benaulim | 11KV Mobor | 4S07-1104 | RURAL | 1360 | 0 | 0 | 24:00:00
77 | MARGAO | 33KV Velim | 11KV Assolna | 4S10-1101 | RURAL | 3397 | 0 | 0 | 24:00:00
78 | MARGAO | 33KV Poinguinim | 11KV Link line | 4S12-1101 | RURAL |  | 0 | 0 | 24:00:00
79 | MARGAO | 33KV Xelpem | 11KV Dando | 4S18-1105 | RURAL | 414 | 0 | 0 | 24:00:00
80 | MAPUSA | 33KV Pernem | 11KV Nagzar | 1S01-1101 | RURAL | 3585 | 29 | 32820 | 23:42 | ABC cable touching line at Borolwada, Alorna, Bhendi tree fallen on line at Chandel, tree branh fallen on line at dadachiwadi, tree branch fallen on line at Alorna, tree branch fallen on line at chichule and HT pole broken, to attend cut jumper near Ayush Hospital, to attend cut jumper at Chichule Dhargal.
81 | MAPUSA | 33KV Tuem | 11KV Morjim | 1S02-1104 | RURAL | 5369 | 0 | 0 | 24:00:00
82 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate II (U/G) | 1S03-1107 | URBAN |  | 9 | 23602.2 | 23:47 | Earth fault at 4 pole structure Karaswada
83 | MAPUSA | 33KV Mapusa | 11KV Sodiem | 1S04-1111 | RURAL | 3424 | 0 | 0 | 24:00:00
84 | MAPUSA | 33KV Nagoa | 11KV Sanqwadi | 1S07-1106 | RURAL | 1215 | 0 | 0 | 24:00:00
85 | MAPUSA | 33KV Saligao | 11KV Candolim church | 1S10-1102 | RURAL | 968 | 0 | 0 | 24:00:00
86 | MAPUSA | 33KV Saligao | 11KV Shervani Calangute | 1S10-1103 | RURAL | 2610 | 8 | 11280 | 23:54 | M/T, O/C E/F
87 | MAPUSA | 33KV Pale | 11KV Nanus | 1S14-1101 | RURAL | 1927 | 0 | 0 | 24:00:00
88 | MAPUSA | 33KV Pale | 11KV Kotumbi | 1S14-1102 | RURAL | 667 | 0 | 0 | 24:00:00
89 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Tivaiwaddo | 1S18-1108 | RURAL |  | 0 | 0 | 24:00:00
90 | PANJIM | 33KV Corlim | 11KV Old Goa | 2S01-1102 | RURAL | 1387 | 0 | 0 | 24:00:00
91 | PANJIM | 33KV Corlim | 11KV Old Industry | 2S01-1105 | URBAN | 82 | 4 | 2760 | 23:58 | Tripped on Earth fault and Over current ,Incomer I Pulled by Old Industry Feeder
92 | PANJIM | 33KV Altinho | 11KV Circuit House | 2S04-1103 | URBAN | 743 | 0 | 0 | 24:00:00
93 | PANJIM | 33KV Bambolim | 11KV MES | 2S05-1102 | RURAL | 4 | 0 | 0 | 24:00:00
94 | PANJIM | 33KV Nagali hills(IT Park) | 11KV OITIYANT | 2S07-1103 | URBAN | 643 | 0 | 0 | 24:00:00
95 | PANJIM | 33KV Colony | 11KV Rajiv Gandhi Kala Mandir | 2S09-1106 | URBAN |  | 0 | 0 | 24:00:00
96 | PANJIM | 33KV Curti | 11KV Sarvoiverem | 2S10-1104 | RURAL | 2878 | 0 | 0 | 24:00:00
97 | MARMAGAO | 33KV Majorda | 11KV Duguem | 3S05-1105 | RURAL | 2317 | 0 | 0 | 24:00:00
98 | MARMAGAO | 33KV Majorda | 11KV Nuvem | 3S05-1106 | RURAL | 2154 | 0 | 0 | 24:00:00
99 | MARMAGAO | 33KV Bogda | ANTARTICA - Headland II | 3S06-1104 | URBAN |  | 0 | 0 | 24:00:00
100 | MARMAGAO | 33KV Bogda | MASJID | 3S06-1105 | RURAL |  | 11 | 17340 | 23:50 | 1)33KV Incomer I supply failed, change over done mormugao full load shifted on mpt2 due to work in Kadamba sub station 2) 33KV Incomer I supply failed, shutdown taken by Verna sub station for repalcing 33 KV bay conductor in Verna sub station yard 3) 33KV Incomer I supply failed, supply failed from Kadamba sub station 4) 33KV Incomer I supply failed, due to power failure from ponda substation yard failure of disc insulator 5) 33KV Incomer I supply failed, supply failed from Verna Sub station 6) 33KV Incomer I supply failed, due to power failure from ponda substation 7) 33KV Incomer I supply failed, supply failed from Verna sub station 8) 33KV Incomer I supply failed, supply failed from Ponda sub station 9) 33KV Incomer I supply failed, supply failed, supply failed from Verna sub station to attend 110 KV disc insulator in the sub station yard
101 | MARGAO | 33KV KRC | 11KV Navelim | 4S05-1101 | RURAL | 3874 | 0 | 0 | 24:00:00
102 | MARGAO | 33KV KRC | 11KV Mandopa | 4S05-1102 | RURAL | 4104 | 28 | 43080 | 23:36 | To change cable and attend jumper
103 | MARGAO | 33KV Benaulim | 11KV Betal Betim | 4S07-1103 | RURAL | 2730 | 12 | 21840 | 23:48 | 33KV Nessai-III incoming supply failure
104 | MARGAO | 33KV Velim | 11KV Kumbia bhat | 4S10-1103 | RURAL | 728 | 0 | 0 | 24:00:00
105 | MARGAO | 33KV Shigao | 11KV Mollem | 4S14-1102 | RURAL | 961 | 0 | 0 | 24:00:00
106 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate I (U/G) | 1S03-1102 | RURAL | 789 | 1 | 3960 | 23:58 | Manually Tripped for changeover
107 | MAPUSA | 33KV Mapusa | 11KV Guirim | 1S04-1109 | RURAL | 3359 | 1 | 2940 | 23:58 | Tripped on EF
108 | MAPUSA | 33KV Bicholim | 11KV Karapur | 1S05-1102 | RURAL | 3502 | 0 | 0 | 24:00:00
109 | MAPUSA | 33KV Nagoa | 11KV Nagoa | 1S07-1104 | RURAL | 598 | 0 | 0 | 24:00:00
110 | MAPUSA | 33KV Porvorim | 11KV Housing board | 1S09-1106 | RURAL | 1653 | 7 | 7260 | 23:56 | E/f, Cable punctured
111 | MAPUSA | 33KV Porvorim | Devashri Feeder | 1S09-1113 | URBAN |  | 0 | 0 | 24:00:00
112 | MAPUSA | 33KV Valpoi | 11KV Nagargao (New) | 1S11-1104 | RURAL | 2243 | 0 | 0 | 24:00:00
113 | MAPUSA | 220KV Amona | 11KV Maina | 1S13-1101 | RURAL | 673 | 8 | 18180 | 23:50 | planned shutdpown to charge UG cable , O/C, E/f
114 | MAPUSA | 33 KV Anjuna | 11KV chapora | 1S15-1104 | URBAN |  | 0 | 0 | 24:00:00
115 | MAPUSA | 33KV Sal | 11KV Mencurem | 1S16-1104 | RURAL |  | 0 | 0 | 24:00:00
116 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Maria Rosa | 1S18-1101 | RURAL |  | 0 | 0 | 24:00:00
117 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Weena | 1S18-1106 | RURAL |  | 0 | 0 | 24:00:00
118 | PANJIM | 33KV Campal | 11KV Ideal School | 2S03-1106 | URBAN | 795 | 0 | 0 | 24:00:00
119 | PANJIM | 33KV NIO | 11KV Odxel | 2S08-1102 | URBAN | 362 | 0 | 0 | 24:00:00
120 | PANJIM | 33KV Dharbandora | 11KV Sonarbag | 2S11-1101 | RURAL | 1414 | 28 | 54360 | 23:30 | 1) to attend jumped 6.3 MVA transformer LV side R phase. 2) replace feeder at Dhada Dharbandora. 3) Tree cuting at Okambv area. 4) jumper open at cattle feed DP.
121 | PANJIM | 33KV Bethora | 11KV Bonbag | 2S13-1103 | RURAL | 1101 | 0 | 0 | 24:00:00
122 | PANJIM | 33KV Kundaim | 11KV Industry I | 2S14-1103 | URBAN | 149 | 19 | 74880 | 23:18 | 33 KV Kundai express old RMU supply disconnected the cable, kundai express connected to 33 KV New RMU in yard
123 | MARMAGAO | 33KV Harbour | 11KV Vasco city | 3S01-1105 | URBAN | 1208 | 12 | 21000 | 23:48 | M/T, outgoing AB switch kept open, gate no. 09 HT AB switch open, vasco city load given to church feeder. utgoing AB switch closed, gate no. 09 HT AB switch closed, Vasco city feeder charged load normalized. Tree cutting done.
124 | MARMAGAO | 33KV Sancoale | 11KV Sicgil | 3S03-1104 | RURAL | 534 | 0 | 0 | 24:00:00
125 | MARMAGAO | 110/33/11 KV Verna | 11KV Quellosim | 3S04-1111 | RURAL |  | 0 | 0 | 24:00:00
126 | MARGAO | 33KV Cuncolim | 11KV Balli | 4S09-1103 | RURAL | 4747 | 26 | 93120 | 23:08 | 1. Newly converted line from OH bare raccoon to OH covered conductor. 2. Failure of may AB switch pad connectors. 3. Failure of disc insulators. 4. failure of LT dist. Transformers. Tracing of faults and restoration of the same resulted in interruptions.
127 | MARGAO | 33KV Poinguinim | 11KV Khotigao | 4S12-1103 | RURAL | 1090 | 0 | 0 | 24:00:00
128 | MAPUSA | 33KV Pernem | 11KV Dhargal | 1S01-1105 | RURAL | 2281 | 0 | 0 | 24:00:00
129 | MAPUSA | 33KV Saligao | 11KV Navy | 1S10-1107 | RURAL | 1 | 0 | 0 | 24:00:00
130 | MAPUSA | 33KV Valpoi | 11KV Thana | 1S11-1103 | RURAL | 2531 | 0 | 0 | 24:00:00
131 | MAPUSA | 33KV Candolim | 11KV Ximer | 1S12-1101 | RURAL | 2403 | 0 | 0 | 24:00:00
132 | MAPUSA | 33 KV Anjuna | 11KV Temvi | 1S15-1101 | URBAN |  | 6 | 12420 | 23:53 | Manually trip for load shedding
133 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Post Office | 1S18-1103 | RURAL |  | 0 | 0 | 24:00:00
134 | PANJIM | 33KV Corlim | 11KV Kadamba | 2S01-1110 | RURAL |  | 8 | 9120 | 23:55 | Tripped on Earth fault and Over current , Jumper cut in sub station Yard
135 | PANJIM | 33KV PILAR | 11KV Neura | 2S06-1101 | RURAL | 2373 | 5 | 6960 | 23:56 | 1) 33 KV Incoming Power supply was manually tripped for Isolator mechanism rectification for 15 Mins on 2/6/2025. 2) 11 KV Neura Feeder was manually tripped for disamntling of ABC cable from 11 KV yard inorder to maintain safety clearance for 50 Mins on 18/6/2025. 3) 11 KV Neura feeder was manually tripped for 15 mins on the request of L.T Staff to clear the Lines from the road on 21/6/2025. 4) 33KV Incoming Power supply failed from 110/33 KV Kadamba-s/s for 12 Mins on 27/6/2025. There were other momentary power interruptions of 2-3 mins durations on Earth fault/Over-current relays reflecting from L.T faults and also due to Change-over at 110/33 KV Kadamba-s/s
136 | PANJIM | 33KV Shiroda | 11KV Borim | 2S12-1101 | RURAL | 4663 | 6 | 11400 | 23:54 | LA Failure at topcola DTC
137 | PANJIM | 33KV Shiroda | 11KV Torla Paz | 2S12-1104 | RURAL |  | 5 | 17760 | 23:50 | 1) Emergency shutdown
138 | MARMAGAO | 33KV Kadamba | 11KV Airport | 3S02-1105 | URBAN | 2464 | 0 | 0 | 24:00:00
139 | MARMAGAO | 33KV Majorda | 11KV Majorda | 3S05-1102 | RURAL | 1137 | 17 | 24300 | 23:46 | Disc insulator punctured at field area carbott T/c Post insulator punctured L.T Line Staff replace Post & Charged.
140 | MARGAO | 33KV Monte Hill | 11KV Lohia-II | 4S03-1107 | URBAN |  | 5 | 6660 | 23:56 | OCR - post insulator problem at Laxmi Plaza replaced
141 | MARGAO | 33KV Canacona | 11KV Gulem | 4S11-1106 | RURAL | 221 | 4 | 25500 | 23:46 | Incoming supply failure and load changeover.
142 | MARGAO | 33KV Pontemol | 11KV IDC | 4S13-1103 | RURAL | 136 | 16 | 23760 | 23:47 | Interrution occurred due to jumper found open at M/s Kansai narolac unit-I, same was attended and feeder charged. Also power interruption occurred during breaker servicing work.
143 | MARGAO | 33KV Shigao | 11KV Collem | 4S14-1101 | RURAL | 1244 | 0 | 0 | 24:00:00
144 | MAPUSA | 220/33KV Thivim | 11KV Tivim | 1S03-1108 | RURAL |  | 0 | 0 | 24:00:00
145 | MAPUSA | 33KV Nagoa | 11KV Arpora | 1S07-1105 | RURAL | 2209 | 0 | 0 | 24:00:00
146 | PANJIM | 33KV EDC | 11KV Kanaka | 2S02-1107 | URBAN |  | 0 | 0 | 24:00:00
147 | PANJIM | 33KV Bambolim | 11KV Santacruz | 2S05-1105 | RURAL | 3673 | 0 | 0 | 24:00:00
148 | PANJIM | 33KV Nagali hills(IT Park) | 11KV MANIPAL | 2S07-1106 | URBAN | 2 | 0 | 0 | 24:00:00
149 | PANJIM | 33KV NIO | 11KV Alto- Nagali | 2S08-1106 | URBAN | 511 | 0 | 0 | 24:00:00
150 | PANJIM | 33KV Colony | 11KV Ponda II | 2S10-1101 | URBAN | 4164 | 1 | 381 | 24:00 | interruption is Zero.
151 | PANJIM | 33KV Curti | 11KV Ponda II | 2S10-1101 | URBAN | 4164 | 0 | 0 | 24:00:00
152 | PANJIM | 33KV Shiroda | 11KV Shiroda Bazar | 2S12-1102 | RURAL | 3102 | 0 | 0 | 24:00:00
153 | MARMAGAO | 33KV Harbour | 11KV Harbour | 3S01-1101 | URBAN | 1392 | 0 | 0 | 24:00:00
154 | MARMAGAO | 110/33/11 KV Verna | 11KV Lokmat | 3S04-1108 | URBAN | 94 | 6 | 10669.8 | 23:54 | Over Current and Earth Fault
155 | MARMAGAO | 33KV Majorda | 11KV Utorda | 3S05-1103 | RURAL | 1783 | 0 | 0 | 24:00:00
156 | MARMAGAO | 33KV Majorda | 11KV Arrosim | 3S05-1104 | RURAL | 1543 | 0 | 0 | 24:00:00
157 | MARGAO | 33KV Aquem | 11KV KHAREBAND II | 4S04-1109 | RURAL |  | 0 | 0 | 24:00:00
158 | MARGAO | 33KV KRC | 11KV MES | 4S05-1103 | RURAL | 2451 | 0 | 0 | 24:00:00
159 | MARGAO | 33KV Carmona | 11KV Cavellossim | 4S08-1104 | RURAL | 1171 | 0 | 0 | 24:00:00
160 | MARGAO | 33KV Cuncolim | 11KV Pattem | 4S09-1107 | RURAL |  | 0 | 0 | 24:00:00
161 | MARGAO | 33KV Canacona | 11KV Palolem | 4S11-1105 | URBAN | 2682 | 0 | 0 | 24:00:00
162 | MAPUSA | 33KV Nagoa | 11KV Baga | 1S07-1107 | RURAL | 2843 | 0 | 0 | 24:00:00
163 | MAPUSA | 33KV Porvorim | 11KV Soccorro | 1S09-1101 | RURAL | 2406 | 0 | 0 | 24:00:00
164 | MAPUSA | 33KV Saligao | 11KV Industry O/H | 1S10-1106 | URBAN | 386 | 0 | 0 | 24:00:00
165 | MAPUSA | 33KV Saligao | 11KV Nerul | 1S10-1108 | RURAL | 3108 | 9 | 13920 | 23:52 | M/T
166 | MAPUSA | 220/33KV Amona | 11 KV Pissurlem IDC | 1S13-1104 | RURAL |  | 2 | 1837.2 | 23:59 | manual trripped for change over
167 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Shivam | 1S18-1104 | RURAL |  | 0 | 0 | 24:00:00
168 | PANJIM | 33KV Corlim | 11KV Molar | 2S01-1106 | RURAL | 1766 | 18 | 121872 | 22:52 | Tripped on Earth fault and Over current , to attend Kadamba Plateau Jumper
169 | PANJIM | 33KV Campal | 11KV City | 2S03-1103 | RURAL | 596 | 0 | 0 | 24:00:00
170 | PANJIM | 33KV Nagali hills(IT Park) | 11KV STATUS | 2S07-1104 | URBAN | 887 | 0 | 0 | 24:00:00
171 | PANJIM | 33KV Colony | 11KV Curti | 2S09-1105 | URBAN |  | 0 | 0 | 24:00:00
172 | PANJIM | 33KV Dharbandora | 11KV Dharbandora | 2S11-1104 | RURAL | 1826 | 43 | 45720 | 23:35 | 1)MT- for servicing work of pristine engineer 2) OCR open Wandala AB switch trip again OCR 3) OCR to disconnect cable at Deulmoll ( Due to likage) 4) Ocr heavy rain and winds open Dharbandora AB switch tree branches fallen on line remove the same near Dharbandora D/P
173 | MARMAGAO | 33KV Sancoale | 11KV College | 3S03-1107 | RURAL | 1168 | 0 | 0 | 24:00:00
174 | MARGAO | 33KV Benaulim | 11KV Colva Exp | 4S07-1107 | URBAN |  | 0 | 0 | 24:00:00
175 | MARGAO | 220/33/11KV Xeldem | 11KV Rivona | 4S15-1102 | RURAL | 2528 | 10 | 11880 | 23:53 | (1)On 02/06/2025 (00:15 min) - M/T, to open tappings at Quinamol s/s. (2)On 02/06/2025 (01:02 min) - Tripped on O/C & E/F, conductor snapped at Shirvoi. (3)On 02/06/2025 (00:35 min) - Tripped on O/C & E/F, conductor snapped. (4)On 03/06/2025 (00:20 min)- M/T on request from concerned authority to attend 33KV jumper of Quinamol line. (5)On 04/06/2025 (00:14 min)- Tripped on EFR, charged after sectionalising AB switch. (6)On 04/06/2025 (00:20 min)- Tripped on O/C, charged after sectionalising AB switch. (7)On 10/06/2025 (00:16 min)- M/T on request from concerned authority to remove creeper touching line at Rivona feeder. (8)On 21/06/2025 (00:17 min)- M/T on request from concerned authority to attend jumper on Rivona feeder. (9)On 22/06/2025 (01:26 min)- Tripped on O/C & E/F, charged after attending fault on line. (10) On 24/06/2025 (00:15 min)- M/T on request from concerned authority to attend open jumper in section-I A/B switch.
176 | MARGAO | 33KV Rivona | 11KV Colomba | 4S16-1103 | RURAL | 316 | 0 | 0 | 24:00:00
177 | MARGAO | 33KV Xelpem | 11KV Sanguem | 4S18-1101 | URBAN | 2566 | 0 | 0 | 24:00:00
178 | MAPUSA | 33KV Pernem | 11KV City | 1S01-1103 | RURAL | 1464 | 16 | 28860 | 23:44 | Changeover of supply, tree bush found on line near police station pernem, L.A found punctured near court DTC.
179 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate | 1S03-1101 | URBAN |  | 5 | 35700 | 23:40 | To attend opened jumper at 4 pole structure karaswada.
180 | MAPUSA | 33KV Nagoa | 11KV Calangute | 1S07-1101 | RURAL | 2986 | 32 | 85194 | 23:13 | Cable Foult
181 | MAPUSA | 33KV Porvorim | 11KV Sangolda | 1S09-1105 | RURAL | 2650 | 7 | 7560 | 23:56 | E/f,o/c, jumper opened
182 | MAPUSA | 33KV Saligao | 11KV Gaurawaddo | 1S10-1109 | URBAN |  | 12 | 37080 | 23:39 | M/T, O/C E/F
183 | MAPUSA | 33KV Valpoi | 11KV City New | 1S11-1105 | RURAL | 2806 | 0 | 0 | 24:00:00
184 | MAPUSA | 33KV Sal | 11KV Kasarpal | 1S16-1103 | RURAL |  | 6 | 9300 | 23:55 | Conductor snapped due to falling of tree
185 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Mark Memorial | 1S18-1105 | URBAN |  | 0 | 0 | 24:00:00
186 | PANJIM | 33KV Campal | 11KV St. Inez | 2S03-1107 | URBAN |  | 0 | 0 | 24:00:00
187 | PANJIM | 33KV Altinho | 11KV Cabo | 2S04-1112 | URBAN | 3821 | 0 | 0 | 24:00:00
188 | PANJIM | 33KV PILAR | 11KV Batim | 2S06-1103 | RURAL | 4199 | 6 | 12060 | 23:53 | 1) 33 KV Incoming Power supply was manually tripped for Isolator mechanism rectification for 15 Mins on 2/6/2025. 2) 11 KV Batim Feeder was manually tripped for disamntling of ABC cable from 11 KV yard inorder to maintain safety clearance for 50 Mins on 18/6/2025. 3) 11 KV Batim feeder was faulty on Earth fault due to Jumper failure which was attended within the time span of 48 mins on 22/06/2025 4) 33KV Incoming Power supply failed from 110/33 KV Kadamba-s/s for 12 Mins on 27/6/2025. There were other momentary power interruptions of 2-3 mins durations on Earth fault/Over-current relays reflecting from L.T faults and also due to Change-over at 110/33 KV Kadamba-s/s
189 | PANJIM | 33KV NIO | 11KV NIO | 2S08-1103 | URBAN | 575 | 0 | 0 | 24:00:00
190 | PANJIM | 33KV Colony | 11KV Bazaar | 2S09-1101 | URBAN | 2570 | 0 | 0 | 24:00:00
191 | PANJIM | 33KV Bethora | 11KV Industrial | 2S13-1104 | URBAN | 246 | 0 | 0 | 24:00:00
192 | PANJIM | 33KV Kundaim | 11KV Kundaim | 2S14-1104 | RURAL | 1252 | 0 | 0 | 24:00:00
193 | MARMAGAO | 33KV Kadamba | 11KV Vasco city | 3S02-1103 | URBAN | 1656 | 9 | 16500 | 23:51 | Delay in charging due to LT work.
194 | MARMAGAO | 33KV Sancoale | 11KV Vasco-I | 3S03-1103 | URBAN | 2369 | 0 | 0 | 24:00:00
195 | MARMAGAO | 110/33/11 KV Verna | 11KV Oxynitro | 3S04-1110 | RURAL |  | 7 | 25831.8 | 23:46 | Feeder was tripping due to low current on sundays. Supply was restored by ring feeding through 11KV IFB Feeder
196 | MARGAO | 33KV Fatorda | 11KV Fatorda | 4S02-1105 | URBAN | 3056 | 0 | 0 | 24:00:00
197 | MARGAO | 33KV Monte Hill | 11KV GVN2 | 4S03-1101 | URBAN |  | 0 | 0 | 24:00:00
198 | MARGAO | 33KV Cuncolim | 11KV IDC I | 4S09-1102 | RURAL | 61 | 0 | 0 | 24:00:00
199 | MARGAO | 33KV Velim | 11KV Betul | 4S10-1102 | RURAL | 1932 | 0 | 0 | 24:00:00
200 | MARGAO | 33KV Poinguinim | 11KV Marli Tirval | 4S12-1102 | RURAL | 889 | 0 | 0 | 24:00:00
201 | MARGAO | 33KV Pontemol | 11KV Town 1 | 4S13-1101 | URBAN | 4338 | 0 | 0 | 24:00:00
202 | MARGAO | 33KV Rivona | 11KV Maina | 4S16-1101 | RURAL | 726 | 40 | 36066 | 23:40 | Failure of AB cable kits & AB Cable / Monkey menace /Fuse of line due falling of huge branches as major part of the line is passning thro' the forest
203 | MAPUSA | 33KV Bicholim | 11KV Assnora | 1S05-1110 | RURAL | 3786 | 0 | 0 | 24:00:00
204 | MAPUSA | 33KV Nagoa | 11KV Sauntawada | 1S07-1102 | RURAL | 1800 | 0 | 0 | 24:00:00
205 | MAPUSA | 33KV Nagoa | 11KV Dharwadkar | 1S07-1108 | RURAL | 2534 | 8 | 4020 | 23:58 | Tripped on EF
206 | MAPUSA | 33KV Porvorim | 11KV Pundalic Nagar | 1S09-1102 | RURAL | 2170 | 0 | 0 | 24:00:00
207 | MAPUSA | 220KV Amona | 11KV Amona Marcel | 1S13-1103 | URBAN |  | 2 | 1837.2 | 23:59 | Trasient fault
208 | PANJIM | 33KV Corlim | 11KV Khumarjau | 2S01-1107 | RURAL | 3047 | 15 | 21600 | 23:48 | Tripped on Earth fault and Over current , Conductor Snapped at Krushi Setu Bridge at Gaundalim
209 | PANJIM | 33KV Corlim | 11KV Diwar | 2S01-1109 | RURAL | 3650 | 15 | 52620 | 23:31 | Tripped on Earth fault and Over current , Jumper cut at Muddi
210 | PANJIM | 33KV EDC | 11KV Ginger | 2S02-1106 | URBAN | 547 | 0 | 0 | 24:00:00
211 | PANJIM | 33KV Campal | 11KV LA- Campal | 2S03-1102 | URBAN | 2920 | 0 | 0 | 24:00:00
212 | PANJIM | 33KV Campal | 11KV Indoor Stadium | 2S03-1104 | URBAN | 1063 | 0 | 0 | 24:00:00
213 | PANJIM | 33KV Bambolim | 11KV Chimbel | 2S05-1106 | RURAL | 4199 | 4 | 7860 | 23:56 | 1) 10 MVA Urja Power Transformer was manually tripped for attending Red-hot on 15/6/2025 for a duration of 20 mins. 2) 11 KV Chimbel feeder was manually tripped on 27/6/2025 for Load shedding as per the instructions of 110/33 KV Substation for a duration of 30 mins. There were other momentary power interruptions of 2-3 mins durations on Earth fault/Over-current relays reflecting from L.T faults and also due to Change-over at 110/33 KV Kadamba-s/s
214 | PANJIM | 33KV NIO | 11KV Rajbhawan | 2S08-1104 | URBAN | 193 | 0 | 0 | 24:00:00
215 | PANJIM | 33KV Colony | 11KV Ponda-I | 2S09-1104 | URBAN | 3332 | 1 | 360 | 24:00 | interruption is Zero.
216 | PANJIM | 33KV Dharbandora | 11KV Bondla | 2S11-1103 | RURAL | 4737 | 4 | 11820 | 23:53 | 1) EFR attend jumper at Bondla feeder 2) OCR open Cine Kamla theater AB switch and taken test charge its OK 3) OCR remove breaker from in & out than taken test charge again trip 4) OCR open Hospital AB switch and charged trip on OCR pulled by Bondla feeder
217 | PANJIM | 33KV Kundaim | 11KV Industry III | 2S14-1105 | URBAN | 83 | 0 | 0 | 24:00:00
218 | MARMAGAO | 33KV Harbour | 11KV Vasco-I | 3S01-1102 | URBAN | 5136 | 0 | 0 | 24:00:00
219 | MARMAGAO | 33KV Sancoale | 11KV Industrial | 3S03-1108 | URBAN | 585 | 11 | 12240 | 23:53 | On 26/06/2025 from 21:45 to 22:10 = 25 mins feeder tripped on earth fault due to fault at HT consumers premises.
220 | MARGAO | 33KV Fatorda | 11KV Borda | 4S02-1104 | URBAN | 4638 | 9 | 8640 | 23:55 | MT to attand jumper at swimming pool
221 | MARGAO | 33KV Aquem | 11KV AQUEM BAIXO | 4S04-1108 | URBAN |  | 0 | 0 | 24:00:00
222 | MARGAO | 33KV Benaulim | 11KV Benaulim | 4S07-1101 | RURAL | 3361 | 6 | 14700 | 23:52 | 33KV Nessai-IV incoming supply failure
223 | MARGAO | 33KV Benaulim | 11KV Trinity | 4S07-1106 | RURAL | 1509 | 17 | 40380 | 23:38 | 33KV Nessai-IV incoming supply failure
224 | MARGAO | 220/33/11KV Xeldem | 11KV Quepem | 4S15-1103 | URBAN | 4866 | 16 | 14040 | 23:52 | (1) On 03/06/2025 (00:16 min)- Tripped on sensitive earth fault relay, AB switch open at Gaonkarwada Quepem, charge holding. (2) On 14/06/2025 (00:22 min)- M/T request from concerned authority to attend AB switch jumper work at Quepem town. (3) On 15/06/2025 (00:42 min)-M/T request from concerned authority for safety purpose to attend failed post insulator on Assolda feeder. (4) On 15/06/2025 (00:17 min)- Tripped on O/C, charge holding after removing coconut leaf.
225 | MARGAO | 33KV Rivona | 11KV Sulcorna | 4S16-1102 | RURAL | 388 | 32 | 370380 | 20:34 | Failure of AB cable kits & AB Cable / Monkey menace /Fuse of line due falling of huge branches as major part of the line is passning thro' the forest
226 | MARGAO | 33KV Waddem | 11KV Netravali | 4S17-1102 | RURAL | 1500 | 0 | 0 | 24:00:00
227 | MAPUSA | 33KV Tuem | 11KV Tuem | 1S02-1103 | RURAL | 738 | 9 | 9540 | 23:55 | change over of supply
228 | MAPUSA | 220/33KV Thivim | 11KV Power Grid | 1S03-1103 | RURAL | 814 | 0 | 0 | 24:00:00
229 | MAPUSA | 33KV Bicholim | 11KV Pilgao | 1S05-1104 | RURAL | 1159 | 11 | 17820 | 23:50 | O/C, E/F , planned shutdown for tree cutting
230 | MAPUSA | 33KV Bicholim | 11KV Bordem | 1S05-1109 | URBAN | 2873 | 10 | 35700 | 23:40 | planned shutdown for tree cutting & maintenance
231 | MAPUSA | 33KV Sanquelim | 11KV Honda | 1S08-1104 | RURAL | 2012 | 13 | 38400 | 23:39 | Planned shutdown for tree cutting and maintenance, E/F
232 | MAPUSA | 33KV Saligao | 11KV Saligao | 1S10-1104 | RURAL | 2726 | 0 | 0 | 24:00:00
233 | MAPUSA | 33KV Candolim | 11KV Sinquerim | 1S12-1105 | RURAL | 1892 | 0 | 0 | 24:00:00
234 | MAPUSA | 33KV Pale | 11KV Barazen | 1S14-1103 | RURAL | 734 | 0 | 0 | 24:00:00
235 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Kamat | 1S18-1107 | RURAL |  | 0 | 0 | 24:00:00
236 | PANJIM | 33KV EDC | 11KV Ribandar | 2S02-1102 | URBAN | 3027 | 0 | 0 | 24:00:00
237 | PANJIM | 33KV Campal | 11KV Market | 2S03-1101 | URBAN | 1000 | 0 | 0 | 24:00:00
238 | PANJIM | 33KV Altinho | 11KV Inox | 2S04-1102 | URBAN | 90 | 0 | 0 | 24:00:00
239 | PANJIM | 33KV Altinho | 11KV Campal | 2S04-1105 | URBAN | 2109 | 3 | 3487.2 | 23:58 | manually tripped to changeover load
240 | PANJIM | 33KV Bambolim | 11KV Merces | 2S05-1104 | RURAL | 3463 | 9 | 14100 | 23:52 | 1) 11 KV Merces feeder was faulty on O/C & E/F fault on 9/6/2025 as the Underground cable was damaged by P.W.D workers while carrying out excavation at Merces Moloca for Pipeline repairs. Feeder was off for about 80 mins 2) 33 KV Bambolim-II incoming power supply failed from 110/33 KV Kadamba-s/s on 15/6/2025 for a duration of 46 mins. 3) 11 KV Merces feeder was manually tripped on 27/6/2025 for Load shedding as per the instructions of 110/33 KV Substation for a duration of 30 mins. There were other momentary power interruptions of 2-3 mins durations on Earth fault/Over-current relays reflecting from L.T faults and also due to Change-over at 110/33 KV Kadamba-s/s
241 | PANJIM | 33KV NIO | 11KV Models | 2S08-1101 | URBAN | 1811 | 0 | 0 | 24:00:00
242 | PANJIM | 33KV Curti | 11KV Usgao | 2S10-1102 | RURAL | 997 | 0 | 0 | 24:00:00
243 | PANJIM | 33KV Madkai | 11KV Madkai | 2S15-1102 | RURAL | 1344 | 0 | 0 | 24:00:00
244 | MARMAGAO | 110/33/11 KV Verna | 11KV Cortalim | 3S04-1107 | RURAL | 4607 | 0 | 0 | 24:00:00
245 | MARGAO | 33KV Raia | 11KV Santamol | 4S01-1103 | RURAL | 783 | 6 | 4020 | 23:58 | EFR - Ganapoga Old RMU open test charge taken feeder tripped, ABS post insulator puncture & one jumper open
246 | MARGAO | 33KV Fatorda | 11KV Chowgule College | 4S02-1103 | URBAN | 4098 | 0 | 0 | 24:00:00
247 | MARGAO | 33KV Monte Hill | 11KV Hari Mandir-II | 4S03-1108 | URBAN |  | 0 | 0 | 24:00:00
248 | MARGAO | 33KV Aquem | 11KV Housing Board O/H | 4S04-1103 | URBAN | 2855 | 0 | 0 | 24:00:00
249 | MARGAO | 33KV Aquem | 11KV Margao III | 4S04-1104 | URBAN | 2492 | 0 | 0 | 24:00:00
250 | MARGAO | 33KV Velim | 11KV Chinchinim | 4S10-1104 | RURAL |  | 0 | 0 | 24:00:00
251 | MARGAO | 33KV Pontemol | 11KV Dabal | 4S13-1107 | RURAL | 2873 | 43 | 43740 | 23:36 | GOAB Switch unit , pin insulator , disc insulatir failure, tree branches fallen, conductor snapped, jumpers open.
252 | MARGAO | 220/33/11KV Xeldem | 11KV Xelvona | 4S15-1101 | RURAL | 2221 | 0 | 0 | 24:00:00
253 | MAPUSA | 220/33KV Thivim | 11KV Sirsaim | 1S03-1106 | RURAL | 1888 | 0 | 0 | 24:00:00
254 | MAPUSA | 33KV Bicholim | 11KV ADVALPAL | 1S05-1105 | RURAL | 1247 | 18 | 57420 | 23:28 | Conductor snapped due to falling of tree, O/c , E/F
255 | MAPUSA | 33KV Bicholim | 11KV City | 1S05-1108 | RURAL | 3526 | 6 | 23040 | 23:47 | for change over of 33KV supply
256 | MAPUSA | 33KV Bicholim | 11KV Kudchirem | 1S05-1111 | RURAL | 1209 | 29 | 33000 | 23:42 | O/C, E/F , Jumper cut
257 | MAPUSA | 33KV Nachinola | 11KV Aldona OH | 1S06-1102 | RURAL | 4570 | 0 | 0 | 24:00:00
258 | MAPUSA | 33KV Sanquelim | 11KV Amona | 1S08-1103 | URBAN | 3050 | 23 | 56760 | 23:28 | Planned shutdown for tree cutting and maintenance
259 | MAPUSA | 33KV Porvorim | 11KV RND | 1S09-1103 | RURAL | 3373 | 0 | 0 | 24:00:00
260 | MAPUSA | 33KV Porvorim | 11KV Chogum | 1S09-1110 | RURAL | 3678 | 0 | 0 | 24:00:00
261 | PANJIM | 33KV Corlim | 11KV Carambolim | 2S01-1104 | RURAL | 3888 | 18 | 22913.4 | 23:47 | Tripped on Earth fault and Over current , Jumper cut at Ella Farm
262 | PANJIM | 33KV Campal | 11KV Adarsh | 2S03-1105 | URBAN | 2705 | 0 | 0 | 24:00:00
263 | PANJIM | 33KV Altinho | 11KV National | 2S04-1101 | URBAN | 1276 | 0 | 0 | 24:00:00
264 | PANJIM | 33KV Altinho | 11KV Manoshanti | 2S04-1106 | URBAN |  | 0 | 0 | 24:00:00
265 | PANJIM | 33KV NIO | 11KV NIO Colony | 2S08-1105 | URBAN | 317 | 0 | 0 | 24:00:00
266 | PANJIM | 33KV Colony | 11KV Khadpabandh | 2S09-1103 | URBAN | 4107 | 5 | 3780 | 23:58 | 17 min(1020 sec) is the actual interruption due to flash over on Rani construction RMU
267 | PANJIM | 33KV Curti | 11KV Curti | 2S10-1108 | URBAN |  | 0 | 0 | 24:00:00
268 | PANJIM | 33KV Kundaim | 11KV Industry II | 2S14-1106 | URBAN | 207 | 1 | 15480 | 23:51 | Manually tripped to attain open jumper at Alcon - Charged stood ok
269 | PANJIM | 33KV Madkai | 11KV Industry II | 2S15-1105 | URBAN | 69 | 20 | 13002 | 23:53 | Overcurrent - Earth fault relay - Charged stood ok
270 | MARMAGAO | 33KV Harbour | 11KV Mangor | 3S01-1104 | URBAN | 4232 | 0 | 0 | 24:00:00
271 | MARMAGAO | 33KV Sancoale | 11KV Dabolim | 3S03-1109 | URBAN |  | 11 | 12780 | 23:53 | On 263/06/2025 from 11:10 to 11:25 = 15 mins, feeder tripped on earth fault due to heavy rain and wind.
272 | MARMAGAO | 110/33/11 KV Verna | 11KV Industrial | 3S04-1103 | URBAN | 114 | 0 | 0 | 24:00:00
273 | MARMAGAO | 33KV Bogda | Brahmasthal - vasco 1 | 3S06-1102 | URBAN |  | 0 | 0 | 24:00:00
274 | MARMAGAO | 33KV Bogda | HARBOUR | 3S06-1103 | URBAN |  | 0 | 0 | 24:00:00
275 | MARGAO | 33KV Raia | 11KV Loutalim | 4S01-1102 | RURAL | 2943 | 0 | 0 | 24:00:00
276 | MARGAO | 33KV Monte Hill | 11KV Adarsh | 4S03-1104 | URBAN | 1578 | 0 | 0 | 24:00:00
277 | MARGAO | 33KV Nessai | 11KV Paroda | 4S06-1102 | RURAL | 2361 | 0 | 0 | 24:00:00
278 | MARGAO | 33KV Benaulim | 11KV Varca | 4S07-1105 | RURAL | 2308 | 0 | 0 | 24:00:00
279 | MARGAO | 33KV Pontemol | 11KV Kalay | 4S13-1104 | RURAL | 177 | 14 | 19680 | 23:49 | tree branches fallen, conductor snapped, jumpers open.
280 | MARGAO | 220/33/11KV Xeldem | 11KV Assolda | 4S15-1104 | RURAL | 1695 | 0 | 0 | 24:00:00
281 | MARGAO | 33KV Waddem | 11KV Bhati | 4S17-1101 | RURAL | 522 | 0 | 0 | 24:00:00
282 | MAPUSA | 33KV Tuem | 11KV Ashvem Cable | 1S02-1105 | RURAL |  | 0 | 0 | 24:00:00
283 | MAPUSA | 33KV Mapusa | 11KV Anjuna | 1S04-1106 | RURAL | 4653 | 0 | 0 | 24:00:00
284 | MAPUSA | 33KV Mapusa | 11KV Assagao | 1S04-1110 | RURAL | 3620 | 13 | 21600 | 23:48 | 1)E/P 86 0PRTD D/F Test charge after opening main section stood ok. 2)M/T to close main section after opening Chari ABS stood ok. 3)M/T to close Chari ABS after open Church ABS and Sonar Bhat stood ok. 4)M/T to close Sonar Bhat ABS but trip on E/F. 5)Trip on E/F Sonar Bhat ABS kept open 6)M/T to close Sonar Bhat ABS after attending the fault 1 Nos LA replaced and Annya Hotel jumper but trip on E/F same kept open & feeder charged. 7)E/F same kept open & feeder charged stood ok. 8)M/T to close Sonar Bhat ABS & all tr. Kept open stood ok. 9)Tripped while closing APKO DTC tripped same kept open feeder charged stood ok.
285 | MAPUSA | 33KV Bicholim | 11KV Ladphem | 1S05-1103 | RURAL | 2232 | 0 | 0 | 24:00:00
286 | MAPUSA | 33KV Bicholim | 11KV Narva | 1S05-1106 | RURAL | 2189 | 35 | 45048 | 23:35 | Maintenance and tree cutting of line
287 | MAPUSA | 33KV Nachinola | 11KV Moira | 1S06-1103 | RURAL | 3008 | 0 | 0 | 24:00:00
288 | MAPUSA | 33KV Nachinola | 11KV Bastora | 1S06-1104 | RURAL | 2213 | 0 | 0 | 24:00:00
289 | MAPUSA | 33KV Sal | 11KV Sal | 1S16-1101 | RURAL |  | 0 | 0 | 24:00:00
290 | PANJIM | 33KV Corlim | 11KV Dhulapi | 2S01-1101 | RURAL | 1284 | 0 | 0 | 24:00:00
291 | PANJIM | 33KV EDC | 11KV Vidyut Bhawan | 2S02-1104 | URBAN | 735 | 0 | 0 | 24:00:00
292 | PANJIM | 33KV Altinho | 11KV Alcon | 2S04-1104 | URBAN | 1407 | 0 | 0 | 24:00:00
293 | PANJIM | 33KV Bambolim | 11KV Donapaula | 2S05-1103 | RURAL | 1904 | 0 | 0 | 24:00:00
294 | PANJIM | 33KV Curti | 11KV OPA | 2S10-1103 | RURAL | 554 | 0 | 0 | 24:00:00
295 | PANJIM | 33KV Kundaim | 11KV Marcel | 2S14-1102 | RURAL | 6565 | 0 | 0 | 24:00:00
296 | PANJIM | 33KV Madkai | 11KV Undir | 2S15-1101 | RURAL | 1773 | 9 | 22500 | 23:47 | underground cable damaged at Paunwada
297 | MARMAGAO | 110/33/11 KV Verna | 11KV Herald | 3S04-1102 | URBAN | 70 | 2 | 7140 | 23:56 | Over Current and Earth Fault
298 | MARMAGAO | 110/33/11 KV Verna | 11KV Jordan | 3S04-1105 | URBAN | 77 | 0 | 0 | 24:00:00
299 | MARMAGAO | 33KV Majorda | 11KV Ramesh Hotel | 3S05-1101 | URBAN | 1 | 0 | 0 | 24:00:00
300 | MARGAO | 33KV Raia | 11KV Raia | 4S01-1101 | RURAL | 2613 | 9 | 8940 | 23:55 | EFR - Tree branch fallen near Govind Pai T/C
301 | MARGAO | 33KV Raia | 11KV Rachol | 4S01-1104 | RURAL | 1233 | 0 | 0 | 24:00:00
302 | MARGAO | 33KV Fatorda | 11KV Old market U/G | 4S02-1102 | URBAN | 4118 | 0 | 0 | 24:00:00
303 | MARGAO | 33KV Aquem | 11KV Housing Board U/G | 4S04-1102 | RURAL | 2148 | 3 | 3480 | 23:58 | EFR- Feeder tripped
304 | MARGAO | 33KV Aquem | 11KV Malbhat | 4S04-1105 | URBAN | 1989 | 0 | 0 | 24:00:00
305 | MARGAO | 33KV Nessai | 11KV MIE | 4S06-1101 | RURAL | 373 | 14 | 18360 | 23:50 | M/T to take test charge on Goa Carbon feeder as Goa Carbon load was shifted on IDC feeder
306 | MARGAO | 33KV Carmona | 11KV XIRO | 4S08-1103 | RURAL | 1213 | 0 | 0 | 24:00:00
307 | MARGAO | 33KV Canacona | 11KV Shristhal | 4S11-1102 | RURAL | 3806 | 8 | 7680 | 23:56 | Incoming supply failure and load changeover.
308 | MARGAO | 33KV Canacona | 11KV Kindlem | 4S11-1103 | RURAL |  | 0 | 0 | 24:00:00
309 | MARGAO | 33KV Pontemol | 11KV Town 2 | 4S13-1106 | URBAN | 1264 | 0 | 0 | 24:00:00
310 | MARGAO | 33KV Pontemol | 11KV HODAR | 4S13-1109 | RURAL |  | 16 | 28140 | 23:44 | Due to electrocution of bird on cruz crusher distribustion transformer. Also power interruption occurred during breaker servicing work.
311 | MARGAO | 33KV Xelpem | 11KV Barazan | 4S18-1103 | RURAL | 1262 | 0 | 0 | 24:00:00
312 | MAPUSA | 33KV Mapusa | 11KV Market | 1S04-1108 | URBAN | 4744 | 4 | 41940 | 23:37 | Cable damaged by PWD works
313 | MAPUSA | 33KV Bicholim | 11KV IDC | 1S05-1101 | RURAL | 325 | 5 | 23640 | 23:47 | 33KV change over of supply at Thivim ss
314 | MAPUSA | 33KV Nagoa | 11KV Parra | 1S07-1103 | RURAL | 2074 | 0 | 0 | 24:00:00
315 | MAPUSA | 33KV Porvorim | 11KV Torda | 1S09-1107 | RURAL | 3879 | 2 | 840 | 24:00 | E/f, O/c.
316 | MAPUSA | 33KV Porvorim | Highland Villa | 1S09-1114 | URBAN |  | 0 | 0 | 24:00:00
317 | MAPUSA | 220KV Amona | 11KV Navelim | 1S13-1102 | RURAL | 2717 | 20 | 68280 | 23:22 | E/F, O/C faults due to disc pucture, tree fallen
318 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Calculo | 1S18-1102 | RURAL |  | 0 | 0 | 24:00:00
319 | PANJIM | 33KV EDC | 11KV Neugi Nagar | 2S02-1105 | URBAN | 1854 | 0 | 0 | 24:00:00
320 | PANJIM | 33KV Altinho | 11KV Lydia Garden | 2S04-1110 | URBAN | 397 | 0 | 0 | 24:00:00
321 | PANJIM | 33KV NIO | 11KV Taligao | 2S08-1108 | URBAN | 875 | 0 | 0 | 24:00:00
322 | PANJIM | 33KV Bethora | 11KV Nirankal | 2S13-1102 | RURAL | 823 | 0 | 0 | 24:00:00
323 | MARMAGAO | 33KV Kadamba | 11KV New Waddem | 3S02-1101 | URBAN | 4502 | 0 | 0 | 24:00:00
324 | MARMAGAO | 33KV Sancoale | 11KV Cortalim | 3S03-1105 | RURAL | 1833 | 0 | 0 | 24:00:00
325 | MARGAO | 33KV Monte Hill | 11KV Lohia | 4S03-1103 | URBAN | 3240 | 0 | 0 | 24:00:00
326 | MARGAO | 33KV KRC | 11KV Navelim UG | 4S05-1105 | URBAN |  | 0 | 0 | 24:00:00
327 | MARGAO | 33KV Cuncolim | 11KV Chinchinim | 4S09-1104 | RURAL | 3157 | 0 | 0 | 24:00:00
328 | MARGAO | 33KV Poinguinim | 11KV Poinguinim | 4S12-1104 | RURAL | 1290 | 4 | 5280 | 23:57 | Incoming supply failure and load changeover.
329 | MAPUSA | 33KV Pernem | 11KV Torse | 1S01-1102 | RURAL | 2343 | 0 | 0 | 24:00:00
330 | MAPUSA | 33KV Mapusa | 11KV Khorlim | 1S04-1107 | URBAN | 2455 | 0 | 0 | 24:00:00
331 | MAPUSA | 33KV Porvorim | 11KV Salai | 1S09-1108 | RURAL | 1197 | 0 | 0 | 24:00:00
332 | MAPUSA | 33KV Porvorim | 11KV GURUDWARA | 1S09-1111 | URBAN |  | 0 | 0 | 24:00:00
333 | MAPUSA | 33KV Saligao | 11KV PILERNE (UG) | 1S10-1110 | RURAL |  | 0 | 0 | 24:00:00
334 | MAPUSA | 33KV Valpoi | 11KV Dabose | 1S11-1106 | RURAL |  | 11 | 29760 | 23:43 | Interruption due to 33KV line failure at valpoi SS
335 | MAPUSA | 33KV Sal | 11KV Ibrampur | 1S16-1102 | RURAL |  | 0 | 0 | 24:00:00
336 | PANJIM | 33KV Altinho | 11KV Tonca Miramar | 2S04-1108 | URBAN | 1682 | 0 | 0 | 24:00:00
337 | PANJIM | 33KV PILAR | 11KV Agasaim | 2S06-1102 | RURAL | 2032 | 0 | 0 | 24:00:00
338 | PANJIM | 33KV Bethora | 11KV Shiroda | 2S13-1101 | RURAL | 419 | 4 | 9540 | 23:55 | 1) EFR- tree Branch fallen on line at rankhol AB switch
339 | MARMAGAO | 33KV Kadamba | 11KV Vasco church | 3S02-1102 | URBAN | 4152 | 19 | 27538.2 | 23:45 | m/t, incoming supply failed mean time shutdown taken to work on airport link abs.
340 | MARMAGAO | 33KV Sancoale | 11KV Vasco-II | 3S03-1106 | RURAL | 2463 | 0 | 0 | 24:00:00
341 | MARGAO | 33KV Monte Hill | 11KV GVN1 | 4S03-1102 | URBAN | 2555 | 5 | 5160 | 23:57 | OCR- Feeder tripped
342 | MARGAO | 33KV Cuncolim | 11KV IDC II | 4S09-1101 | RURAL | 118 | 14 | 52860 | 23:31 | 1.) Insulcoating of IDC feeder panel carried out since there was flashover due to ingress of moisture during monsoon.2.) Flash over of cubicle of many HTCs.
343 | MARGAO | 33KV Poinguinim | 11KV Loliem | 4S12-1105 | RURAL | 2515 | 11 | 10080 | 23:54 | Incoming supply failure and load changeover.