## 11 KV May 2025
Sl No | Town Name | Substation | Feeder Name | Feeder Code | Rural/Urban | No_of_Consumers | No_of_Outages | Duration_of_Outage_Sec | Average_Hours_of_Steady_Supply | Reason for power disruptions
1 | MAPUSA | 220/33KV Thivim | 11KV Tivim | 1S03-1108 | RURAL |  | 0 | 0 | 24:00:00
2 | MAPUSA | 33KV Nagoa | 11KV Arpora | 1S07-1105 | RURAL | 2209 | 0 | 0 | 24:00:00
3 | PANJIM | 33KV EDC | 11KV Kanaka | 2S02-1107 | URBAN |  | 0 | 0 | 24:00:00
4 | PANJIM | 33KV Bambolim | 11KV Santacruz | 2S05-1105 | RURAL | 3673 | 0 | 0 | 24:00:00
5 | PANJIM | 33KV Nagali hills(IT Park) | 11KV MANIPAL | 2S07-1106 | URBAN | 2 | 0 | 0 | 24:00:00
6 | PANJIM | 33KV NIO | 11KV Alto-Nagali | 2S08-1106 | URBAN | 511 | 0 | 0 | 24:00:00
7 | PANJIM | 33KV Colony | 11KV Ponda II | 2S10-1101 | URBAN | 4164 | 0 | 0 | 24:00:00
8 | PANJIM | 33KV Curti | 11KV Ponda II | 2S10-1101 | URBAN | 4164 | 0 | 0 | 24:00:00
9 | PANJIM | 33KV Shiroda | 11KV Shiroda Bazar | 2S12-1102 | RURAL | 3102 | 0 | 0 | 24:00:00
10 | MARMAGAO | 33KV Harbour | 11KV Harbour | 3S01-1101 | URBAN | 1392 | 0 | 0 | 24:00:00
11 | MARMAGAO | 110/33/11 KV Verna | 11KV Lokmat | 3S04-1108 | URBAN | 94 | 1 | 1749 | 23:59 | Tripped on Overcurrent fault
12 | MARMAGAO | 33KV Majorda | 11KV Utorda | 3S05-1103 | RURAL | 1783 | 0 | 0 | 24:00:00
13 | MARMAGAO | 33KV Majorda | 11KV Arrosim | 3S05-1104 | RURAL | 1543 | 0 | 0 | 24:00:00
14 | MARGAO | 33KV Aquem | 11KV KHAREBAND II | 4S04-1109 | RURAL |  | 0 | 0 | 24:00:00
15 | MARGAO | 33KV KRC | 11KV MES | 4S05-1103 | RURAL | 2451 | 0 | 0 | 24:00:00
16 | MARGAO | 33KV Carmona | 11KV Cavellossim | 4S08-1104 | RURAL | 1171 | 0 | 0 | 24:00:00
17 | MARGAO | 33KV Cuncolim | 11KV Pattem | 4S09-1107 | RURAL |  | 0 | 0 | 24:00:00
18 | MARGAO | 33KV Canacona | 11KV Palolem | 4S11-1105 | URBAN | 2682 | 0 | 0 | 24:00:00
19 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate I (U/G) | 1S03-1102 | RURAL | 789 | 1 | 5520 | 23:57 | Manually tripped
20 | MAPUSA | 33KV Mapusa | 11KV Guirim | 1S04-1109 | RURAL | 3359 | 4 | 5280 | 23:57 | Changeover
21 | MAPUSA | 33KV Bicholim | 11KV Karapur | 1S05-1102 | RURAL | 3502 | 4 | 2700 | 23:58 | For maintenance at station yard
22 | MAPUSA | 33KV Nagoa | 11KV Nagoa | 1S07-1104 | RURAL | 598 | 0 | 0 | 24:00:00
23 | MAPUSA | 33KV Porvorim | 11KV Housing board | 1S09-1106 | RURAL | 1653 | 2 | 3720 | 23:58 | E/f. Cable faulty
24 | MAPUSA | 33KV Porvorim | Devashri Feeder | 1S09-1113 | URBAN |  | 0 | 0 | 24:00:00
25 | MAPUSA | 33KV Valpoi | 11KV Nagargao (New) | 1S11-1104 | RURAL | 2243 | 0 | 0 | 24:00:00
26 | MAPUSA | 220KV Amona | 11KV Maina | 1S13-1101 | RURAL | 673 | 1 | 1440 | 23:59 | For charging of Maina UG cable
27 | MAPUSA | 33 KV Anjuna | 11KV chapora | 1S15-1104 | URBAN |  | 0 | 0 | 24:00:00
28 | MAPUSA | 33KV Sal | 11KV Mencurem | 1S16-1104 | RURAL |  | 0 | 0 | 24:00:00
29 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Maria Rosa | 1S18-1101 | RURAL |  | 0 | 0 | 24:00:00
30 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Weena | 1S18-1106 | RURAL |  | 0 | 0 | 24:00:00
31 | PANJIM | 33KV Campal | 11KV Ideal School | 2S03-1106 | URBAN | 795 | 0 | 0 | 24:00:00
32 | PANJIM | 33KV NIO | 11KV Odxel | 2S08-1102 | URBAN | 362 | 0 | 0 | 24:00:00
33 | PANJIM | 33KV Dharbandora | 11KV Sonarbag | 2S11-1101 | RURAL | 1414 | 3 | 3720 | 23:58 | 1)OCR charge feeder due to autorecloser trip of 33kv 2) OCR declare faulty (tree fallen on line 3) MT to open Nestle & RTO as switch and than charge feeder ok 4) MT RMU cable connection for DTC at Shekre,Keriyan& Okam 5) MT HT/LT line shifting at Bhumikanagar
34 | PANJIM | 33KV Bethora | 11KV Bonbag | 2S13-1103 | RURAL | 1101 | 1 | 355.2 | 24:00 | 1) MT to erect new RCC pole 2)OCR test charge not holding after petroling line remove coconut plam fallen on lineat Padi T/C 3) MT to attend 11kv line tree cutting near M/C Dowell area after complete work line charge holding
35 | PANJIM | 33KV Kundaim | 11KV Industry I | 2S14-1103 | URBAN | 149 | 1 | 660 | 24:00 | 11 KV ncomer cable failure
36 | MARMAGAO | 33KV Harbour | 11KV Vasco city | 3S01-1105 | URBAN | 1208 | 8 | 25560 | 23:46 | L.C. given to JE Kulakarni & JE Praveen to do maintenance work. L.C. return at 13:33 by JE Kulkarni & at 12:45 by JE Praveen.
37 | MARMAGAO | 33KV Sancoale | 11KV Sicgil | 3S03-1104 | RURAL | 534 | 0 | 0 | 24:00:00
38 | MARMAGAO | 110/33/11 KV Verna | 11KV Quellosim | 3S04-1111 | RURAL |  | 0 | 0 | 24:00:00
39 | MARGAO | 33KV Cuncolim | 11KV Balli | 4S09-1103 | RURAL | 4747 | 3 | 4080 | 23:58 | Due to the replacement of conductor for the tendered work of conversion of OH bare conductor to covered cable/conductor.
40 | MARGAO | 33KV Poinguinim | 11KV Khotigao | 4S12-1103 | RURAL | 1090 | 0 | 0 | 24:00:00
41 | MAPUSA | 33KV Mapusa | 11KV Market | 1S04-1108 | URBAN | 4744 | 5 | 4800 | 23:57 | Change over
42 | MAPUSA | 33KV Bicholim | 11KV IDC | 1S05-1101 | RURAL | 325 | 2 | 1020 | 23:59 | For 33KV Changeover, Maintenace shutdown
43 | MAPUSA | 33KV Nagoa | 11KV Parra | 1S07-1103 | RURAL | 2074 | 0 | 0 | 24:00:00
44 | MAPUSA | 33KV Porvorim | 11KV Torda | 1S09-1107 | RURAL | 3879 | 2 | 1080 | 23:59 | O/c,E/f
45 | MAPUSA | 33KV Porvorim | Highland Villa | 1S09-1114 | URBAN |  | 0 | 0 | 24:00:00
46 | MAPUSA | 220KV Amona | 11KV Navelim | 1S13-1102 | RURAL | 2717 | 19 | 26340 | 23:45 | Earth fault,line maintenance and tree cutting
47 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Calculo | 1S18-1102 | RURAL |  | 0 | 0 | 24:00:00
48 | PANJIM | 33KV EDC | 11KV Neugi Nagar | 2S02-1105 | URBAN | 1854 | 0 | 0 | 24:00:00
49 | PANJIM | 33KV Altinho | 11KV Lydia Garden | 2S04-1110 | URBAN | 397 | 0 | 0 | 24:00:00
50 | PANJIM | 33KV NIO | 11KV Taligao | 2S08-1108 | URBAN | 875 | 0 | 0 | 24:00:00
51 | PANJIM | 33KV Bethora | 11KV Nirankal | 2S13-1102 | RURAL | 823 | 0 | 0 | 24:00:00
52 | MARMAGAO | 33KV Kadamba | 11KV New Waddem | 3S02-1101 | URBAN | 4502 | 0 | 0 | 24:00:00
53 | MARMAGAO | 33KV Sancoale | 11KV Cortalim | 3S03-1105 | RURAL | 1833 | 0 | 0 | 24:00:00
54 | MARGAO | 33KV Monte Hill | 11KV Lohia | 4S03-1103 | URBAN | 3240 | 0 | 0 | 24:00:00
55 | MARGAO | 33KV KRC | 11KV Navelim UG | 4S05-1105 | URBAN |  | 0 | 0 | 24:00:00
56 | MARGAO | 33KV Cuncolim | 11KV Chinchinim | 4S09-1104 | RURAL | 3157 | 0 | 0 | 24:00:00
57 | MARGAO | 33KV Poinguinim | 11KV Poinguinim | 4S12-1104 | RURAL | 1290 | 2 | 1380 | 23:59 | Incoming supply failure and load changeover.
58 | MAPUSA | 33KV Tuem | 11KV Tuem | 1S02-1103 | RURAL | 738 | 5 | 3480 | 23:58 | Tripped on E/F- Conductor snapped at Atchut House, Tripped on O/C , R/Y- open jumper attended & charged.
59 | MAPUSA | 220/33KV Thivim | 11KV Power Grid | 1S03-1103 | RURAL | 814 | 0 | 0 | 24:00:00
60 | MAPUSA | 33KV Bicholim | 11KV Pilgao | 1S05-1104 | RURAL | 1159 | 3 | 4620 | 23:57 | Planned Shutdown, Line Faults E/F Inuslator failure, O/C Tree fallen
61 | MAPUSA | 33KV Bicholim | 11KV Bordem | 1S05-1109 | URBAN | 2873 | 1 | 1140 | 23:59 | Planned Shutdown
62 | MAPUSA | 33KV Sanquelim | 11KV Honda | 1S08-1104 | RURAL | 2012 | 4 | 4800 | 23:57 | For maintenance and tree cutting
63 | MAPUSA | 33KV Saligao | 11KV Saligao | 1S10-1104 | RURAL | 2726 | 0 | 0 | 24:00:00
64 | MAPUSA | 33KV Candolim | 11KV Sinquerim | 1S12-1105 | RURAL | 1892 | 0 | 0 | 24:00:00
65 | MAPUSA | 33KV Pale | 11KV Barazen | 1S14-1103 | RURAL | 734 | 0 | 0 | 24:00:00
66 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Kamat | 1S18-1107 | RURAL |  | 0 | 0 | 24:00:00
67 | PANJIM | 33KV EDC | 11KV Ribandar | 2S02-1102 | URBAN | 3027 | 0 | 0 | 24:00:00
68 | PANJIM | 33KV Campal | 11KV Market | 2S03-1101 | URBAN | 1000 | 0 | 0 | 24:00:00
69 | PANJIM | 33KV Altinho | 11KV Inox | 2S04-1102 | URBAN | 90 | 0 | 0 | 24:00:00
70 | PANJIM | 33KV Altinho | 11KV Campal | 2S04-1105 | URBAN | 2109 | 2 | 963 | 23:59 | Transient Tripping
71 | PANJIM | 33KV Bambolim | 11KV Merces | 2S05-1104 | RURAL | 3463 | 3 | 2760 | 23:58 | Load shedding imposed by 110/33 KV Kadamba Plateau substation on account of Planned shutdown arranged by 220 KV Tivim Substation on 10/5/2025. 11 KV Feeders were manually tripped on rotational basis from 9:30 am to 4:00 pm.
72 | PANJIM | 33KV NIO | 11KV Models | 2S08-1101 | URBAN | 1811 | 0 | 0 | 24:00:00
73 | PANJIM | 33KV Curti | 11KV Usgao | 2S10-1102 | RURAL | 997 | 0 | 0 | 24:00:00
74 | PANJIM | 33KV Madkai | 11KV Madkai | 2S15-1102 | RURAL | 1344 | 0 | 0 | 24:00:00
75 | MARMAGAO | 110/33/11 KV Verna | 11KV Cortalim | 3S04-1107 | RURAL | 4607 | 0 | 0 | 24:00:00
76 | MARGAO | 33KV Raia | 11KV Santamol | 4S01-1103 | RURAL | 783 | 1 | 360 | 24:00 | 2 Post insulator & LA punctured on 1st DT of Santemol feeder pulled 11 KV Raia feeder during fault. Occurred during thunderstorm
77 | MARGAO | 33KV Fatorda | 11KV Chowgule College | 4S02-1103 | URBAN | 4098 | 0 | 0 | 24:00:00
78 | MARGAO | 33KV Monte Hill | 11KV Hari Mandir-II | 4S03-1108 | URBAN |  | 0 | 0 | 24:00:00
79 | MARGAO | 33KV Aquem | 11KV Housing Board O/H | 4S04-1103 | URBAN | 2855 | 0 | 0 | 24:00:00
80 | MARGAO | 33KV Aquem | 11KV Margao III | 4S04-1104 | URBAN | 2492 | 0 | 0 | 24:00:00
81 | MARGAO | 33KV Velim | 11KV Chinchinim | 4S10-1104 | RURAL |  | 0 | 0 | 24:00:00
82 | MARGAO | 33KV Pontemol | 11KV Dabal | 4S13-1107 | RURAL | 2873 | 3 | 6660 | 23:56 | Interrutions due to insulator failure, GOAB switch unit failure, Bird fault.
83 | MARGAO | 220/33/11KV Xeldem | 11KV Xelvona | 4S15-1101 | RURAL | 2221 | 0 | 0 | 24:00:00
84 | MAPUSA | 33KV Pernem | 11KV Sawal | 1S01-1104 | RURAL | 453 | 5 | 9180 | 23:55 | Post insulator faults on IDC AB switch, Lightening arrestor failure on DP at ITI, tree branches fallen on line at Sawalwada.
85 | MAPUSA | 33KV Tuem | 11KV Industry | 1S02-1101 | URBAN |  | 7 | 11160 | 23:54 | To attend open jumper, Tripped O/C, RB Phase, MT as per request by JE Prajyot to attend LT snapped conductor in industrial area , tripped on E/F, MT to replace punctured disck
86 | MAPUSA | 220/33KV Thivim | 11KV Colvale | 1S03-1104 | RURAL | 3897 | 0 | 0 | 24:00:00
87 | MAPUSA | 33KV Mapusa | 11KV Duler | 1S04-1102 | URBAN | 7977 | 6 | 34860 | 23:41 | Cable damaged by PWD
88 | MAPUSA | 33KV Mapusa | 11KV City | 1S04-1103 | RURAL | 3601 | 0 | 0 | 24:00:00
89 | MAPUSA | 33KV Sanquelim | 11KV Poriem | 1S08-1101 | RURAL | 3862 | 0 | 0 | 24:00:00
90 | MAPUSA | 33KV Valpoi | 11KV Saleli | 1S11-1102 | RURAL | 3024 | 8 | 15120 | 23:52 | For tree cutting / Maintenace work.
91 | MAPUSA | 33KV Candolim | 11KV Highland | 1S12-1106 | RURAL | 2331 | 0 | 0 | 24:00:00
92 | MAPUSA | 33 KV Anjuna | 11KV vagator | 1S15-1102 | RURAL |  | 0 | 0 | 24:00:00
93 | PANJIM | 33KV EDC | 11KV Old bus stand | 2S02-1101 | URBAN | 915 | 0 | 0 | 24:00:00
94 | PANJIM | 33KV Curti | 11KV Durbhat | 2S10-1106 | RURAL | 2896 | 0 | 0 | 24:00:00
95 | PANJIM | 33KV Madkai | 11KV Karanzal | 2S15-1103 | RURAL | 697 | 8 | 174480 | 22:23 | earth fault trip, jumper opened and trip finding delay, insulator failure in S/S
96 | MARMAGAO | 33KV Sancoale | 11KV Cansualim | 3S03-1102 | RURAL | 2789 | 2 | 2640 | 23:59 | On 9/5/25 feeder tripped on overcurrent relay, 17/5/25 feeder tripped twice on earth fault, 18/5/25 a 11KV Pin insulator was found faulty at velsao, on 28/5/25 tree had fallen on HT line at velsao, 29/5/25 shutdown was availed by majorda staff for removing of guarding.
97 | MARMAGAO | 110/33/11 KV Verna | 11KV Verna | 3S04-1101 | RURAL | 3069 | 0 | 0 | 24:00:00
98 | MARMAGAO | 110/33/11 KV Verna | 11KV Nagoa | 3S04-1106 | RURAL | 1407 | 3 | 3840 | 23:58 | Tripped on Earth Fault
99 | MARGAO | 33KV Raia | 11KV Curtorim | 4S01-1105 | RURAL | 3128 | 0 | 0 | 24:00:00
100 | MARGAO | 33KV Fatorda | 11KV Ambaji | 4S02-1101 | URBAN | 3412 | 0 | 0 | 24:00:00
101 | MARGAO | 33KV Monte Hill | 11KV Mutt | 4S03-1106 | URBAN | 578 | 0 | 0 | 24:00:00
102 | MARGAO | 33KV Aquem | 11KV Margao I | 4S04-1107 | URBAN |  | 4 | 4440 | 23:58 | OCR - relay reset charged tripped on same declared faulty charged after opening due to moisture
103 | MARGAO | 33KV Nessai | 11KV Goa Carbon | 4S06-1104 | URBAN | 2445 | 0 | 0 | 24:00:00
104 | MARGAO | 33KV Carmona | 11KV Janoth Bazar | 4S08-1102 | URBAN | 1416 | 0 | 0 | 24:00:00
105 | MARGAO | 33KV Cuncolim | 11KV Cuncolim | 4S09-1105 | RURAL | 3243 | 0 | 0 | 24:00:00
106 | MARGAO | 33KV Pontemol | 11KV Panchwadi | 4S13-1102 | RURAL | 3115 | 0 | 0 | 24:00:00
107 | MARGAO | 33KV Xelpem | 11KV Malkarne | 4S18-1104 | RURAL | 996 | 0 | 0 | 24:00:00
108 | MAPUSA | 33KV Pernem | 11KV Dhargal | 1S01-1105 | RURAL | 2281 | 0 | 0 | 24:00:00
109 | MAPUSA | 33KV Saligao | 11KV Navy | 1S10-1107 | RURAL | 1 | 0 | 0 | 24:00:00
110 | MAPUSA | 33KV Valpoi | 11KV Thana | 1S11-1103 | RURAL | 2531 | 0 | 0 | 24:00:00
111 | MAPUSA | 33KV Candolim | 11KV Ximer | 1S12-1101 | RURAL | 2403 | 0 | 0 | 24:00:00
112 | MAPUSA | 33 KV Anjuna | 11KV Temvi | 1S15-1101 | URBAN |  | 2 | 5100 | 23:57 | load shedding
113 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Post Office | 1S18-1103 | RURAL |  | 0 | 0 | 24:00:00
114 | PANJIM | 33KV Corlim | 11KV Kadamba | 2S01-1110 | RURAL |  | 2 | 1560 | 23:59 | Tripped on over current as cable damaged at Landscape.
115 | PANJIM | 33KV PILAR | 11KV Neura | 2S06-1101 | RURAL | 2373 | 3 | 2160 | 23:59 | Load shedding imposed by 110/33 KV Kadamba Plateau substation on account of Planned shutdown arranged by 220 KV Tivim Substation on 10/5/2025. 11 KV Feeders were manually tripped on rotational basis from 9:30 am to 4:00 pm.
116 | PANJIM | 33KV Shiroda | 11KV Borim | 2S12-1101 | RURAL | 4663 | 0 | 0 | 24:00:00
117 | PANJIM | 33KV Shiroda | 11KV Torla Paz | 2S12-1104 | RURAL |  | 0 | 0 | 24:00:00
118 | MARMAGAO | 33KV Kadamba | 11KV Airport | 3S02-1105 | URBAN | 2464 | 0 | 0 | 24:00:00
119 | MARMAGAO | 33KV Majorda | 11KV Majorda | 3S05-1102 | RURAL | 1137 | 8 | 33180 | 23:42 | 1) Planned shutdown for maintenance work at 110/33 Kv EHV Verna Sub-station also taken shutdown on 33/11 KV Shutdwon for maintenance. 2) 10 MVA Transformer master relay , heavy spark ,taken shut down to LV bushing side jumper attend. 3) Manually tripped at 15.03 to 15.34 to open 9 Pole ABS near Queeny Upasnagar . 33 KV Majorda CKT-I cable burned also 33 KV majorda CKt-I burnt, after opening 9 Pole ABS & 33 KV Majorda Ckt-I Charged ok.
120 | MARGAO | 33KV Monte Hill | 11KV Lohia-II | 4S03-1107 | URBAN |  | 2 | 3900 | 23:58 | I/F - due to main incomer failure
121 | MARGAO | 33KV Canacona | 11KV Gulem | 4S11-1106 | RURAL | 221 | 0 | 0 | 24:00:00
122 | MARGAO | 33KV Pontemol | 11KV IDC | 4S13-1103 | RURAL | 136 | 1 | 600 | 24:00 | To check red hot on 11KV Bay
123 | MARGAO | 33KV Shigao | 11KV Collem | 4S14-1101 | RURAL | 1244 | 0 | 0 | 24:00:00
124 | MAPUSA | 220/33KV Thivim | 11KV Thivim Village | 1S03-1105 | RURAL | 3173 | 3 | 2940 | 23:58 | 1)Trip on Over Current Earth Fault 2)Manully trip to open Lala Tapping 3)Tree found on line
125 | MAPUSA | 33KV Bicholim | 11KV MAYEM | 1S05-1107 | RURAL | 756 | 7 | 18660 | 23:50 | Planned Shutdown, Line Faults E/F Inuslator failure, O/C Tree fallen
126 | MAPUSA | 33KV Sanquelim | 11KV Sanquelim | 1S08-1102 | URBAN | 1599 | 0 | 0 | 24:00:00
127 | MAPUSA | 33KV Porvorim | 11KV Porvorim Bazar | 1S09-1109 | RURAL | 1849 | 3 | 3480 | 23:58 | E/f. Conductor snapped, jumper opened.
128 | MAPUSA | 33KV Porvorim | Audit bhavan | 1S09-1112 | URBAN |  | 0 | 0 | 24:00:00
129 | MAPUSA | 33KV Valpoi | 11KV Bhironda | 1S11-1101 | RURAL | 2606 | 7 | 39600 | 23:38 | For operating GOAB Switch, for tree cutting / Maintenace work.
130 | MAPUSA | 33KV Candolim | 11KV Candolim | 1S12-1103 | RURAL | 2097 | 0 | 0 | 24:00:00
131 | PANJIM | 33KV Nagali hills(IT Park) | 11KV BSNL | 2S07-1105 | URBAN |  | 0 | 0 | 24:00:00
132 | PANJIM | 33KV Madkai | 11KV Industry I | 2S15-1104 | URBAN | 31 | 4 | 3360 | 23:58 | Earth fault trip,Overcurrent fault and jumper opened
133 | MARMAGAO | 33KV Bogda | HEADLAND | 3S06-1101 | URBAN |  | 0 | 0 | 24:00:00
134 | MARGAO | 33KV Monte Hill | 11KV Hari Mandir | 4S03-1105 | URBAN | 4581 | 3 | 4396.8 | 23:58 | I/F - due to main incomer failure
135 | MARGAO | 33KV Aquem | 11KV Khareband | 4S04-1101 | URBAN | 5182 | 0 | 0 | 24:00:00
136 | MARGAO | 33KV Carmona | 11KV Zalor | 4S08-1101 | RURAL | 546 | 6 | 44583 | 23:35 | 33KV Velim-II Incoming Supply Failed
137 | MARGAO | 33KV Cuncolim | 11KV Dharmapur | 4S09-1106 | RURAL | 3011 | 0 | 0 | 24:00:00
138 | MARGAO | 33KV Pontemol | 11KV Bansai | 4S13-1105 | RURAL | 4480 | 2 | 7380 | 23:56 | To replace failed LA and also to attend loose jumper on 11KV yard. Alternate supply were given on Bansai feeder.
139 | MAPUSA | 33KV Bicholim | 11KV Assnora | 1S05-1110 | RURAL | 3786 | 0 | 0 | 24:00:00
140 | MAPUSA | 33KV Nagoa | 11KV Sauntawada | 1S07-1102 | RURAL | 1800 | 0 | 0 | 24:00:00
141 | MAPUSA | 33KV Nagoa | 11KV Dharwadkar | 1S07-1108 | RURAL | 2534 | 5 | 6240 | 23:57 | Cable foult,RMU flash over, Jumper cut on 33Kv Mapusa-III Ckt
142 | MAPUSA | 33KV Porvorim | 11KV Pundalic Nagar | 1S09-1102 | RURAL | 2170 | 0 | 0 | 24:00:00
143 | MAPUSA | 220KV Amona | 11KV Amona Marcel | 1S13-1103 | URBAN |  | 0 | 0 | 24:00:00
144 | PANJIM | 33KV Corlim | 11KV Khumarjau | 2S01-1107 | RURAL | 3047 | 1 | 360 | 24:00 | Tripped due to earthfault and over current.
145 | PANJIM | 33KV Corlim | 11KV Diwar | 2S01-1109 | RURAL | 3650 | 2 | 2160 | 23:59 | Tripped on Earth fault, found crow on line at Vanxem Diwar.
146 | PANJIM | 33KV EDC | 11KV Ginger | 2S02-1106 | URBAN | 547 | 0 | 0 | 24:00:00
147 | PANJIM | 33KV Campal | 11KV LA-Campal | 2S03-1102 | URBAN | 2920 | 0 | 0 | 24:00:00
148 | PANJIM | 33KV Campal | 11KV Indoor Stadium | 2S03-1104 | URBAN | 1063 | 0 | 0 | 24:00:00
149 | PANJIM | 33KV Bambolim | 11KV Chimbel | 2S05-1106 | RURAL | 4199 | 0 | 0 | 24:00:00
150 | PANJIM | 33KV NIO | 11KV Rajbhawan | 2S08-1104 | URBAN | 193 | 0 | 0 | 24:00:00
151 | PANJIM | 33KV Colony | 11KV Ponda-I | 2S09-1104 | URBAN | 3332 | 0 | 0 | 24:00:00
152 | PANJIM | 33KV Dharbandora | 11KV Bondla | 2S11-1103 | RURAL | 4737 | 6 | 7980 | 23:56 | 1) MT to erect new pole at Ponsulem 2) MT HT line shifting at Ponsulem bypass road 3) MT HT/LT line shifting at Ponsulem 4) MT heavy spark on AB switch at Ponsulem (bladge loose) 5) MT to replace transformer at Bhumikanagar
153 | PANJIM | 33KV Kundaim | 11KV Industry III | 2S14-1105 | URBAN | 83 | 0 | 0 | 24:00:00
154 | MARMAGAO | 33KV Harbour | 11KV Vasco-I | 3S01-1102 | URBAN | 5136 | 0 | 0 | 24:00:00
155 | MARMAGAO | 33KV Sancoale | 11KV Industrial | 3S03-1108 | URBAN | 585 | 3 | 1380 | 23:59 | Feeder was manually tripped on 18/5/025 as per planned shutdown availed for entire Mormugao taluka.
156 | MARGAO | 33KV Fatorda | 11KV Borda | 4S02-1104 | URBAN | 4638 | 0 | 0 | 24:00:00
157 | MARGAO | 33KV Aquem | 11KV AQUEM BAIXO | 4S04-1108 | URBAN |  | 0 | 0 | 24:00:00
158 | MARGAO | 33KV Benaulim | 11KV Benaulim | 4S07-1101 | RURAL | 3361 | 5 | 6240 | 23:57 | 33KV Nessai-IV Incoming Supply Failed
159 | MARGAO | 33KV Benaulim | 11KV Trinity | 4S07-1106 | RURAL | 1509 | 6 | 6480 | 23:56 | 33KV Nessai-IV Incoming Supply Failed
160 | MARGAO | 220/33/11KV Xeldem | 11KV Quepem | 4S15-1103 | URBAN | 4866 | 9 | 8460 | 23:55 | (1) On 15/05/2025 (00:36 min) - feeder tripped on EFR and o/c. Feeder charged after isolating R.M.U. at Ambaulim. (2) On 20/05/2025 (00:23 min) - feeder tripped on o/c. feeder charged after opening A/B switch at Gaonkarwada. (3) On 22/05/2025 (00:12 min) - feeder tripped on o/c. feeder charged after opening A/B switch at Quepem market. (4) On 24/05/2025 (00:16 min) - feeder M/T due to heavy rain and wind. charged ok. (5) On 24/05/2025 (00:17 min) - feeder tripped on E/F and o/c. Feeder charged after isolating R.M.U. at Gaonkarwada. (6) On 26/05/2025 (00:12 min) - feeder tripped on E/F and o/c. Feeder charged after isolating R.M.U. at Gaonkarwada.
161 | MARGAO | 33KV Rivona | 11KV Sulcorna | 4S16-1102 | RURAL | 388 | 11 | 19500 | 23:49 | Due to frequent failure of AB cable termination kit and planned shutdown taken for tree cutting
162 | MARGAO | 33KV Waddem | 11KV Netravali | 4S17-1102 | RURAL | 1500 | 0 | 0 | 24:00:00
163 | MAPUSA | 33KV Mapusa | 11KV Althino | 1S04-1105 | URBAN | 6119 | 0 | 0 | 24:00:00
164 | MAPUSA | 33KV Mapusa | 11KV Siolim | 1S04-1112 | RURAL | 3827 | 0 | 0 | 24:00:00
165 | MAPUSA | 33KV Nachinola | 11KV Aldona UG | 1S06-1105 | RURAL |  | 3 | 4320 | 23:58 | Declared foulty on EF, lizard touches interlinking line at aldona.
166 | MAPUSA | 33KV Nagoa | 11KV AGARWADDO | 1S07-1109 | RURAL |  | 8 | 9820.2 | 23:55 | Cable Foult
167 | MAPUSA | 33KV Saligao | 11KV Betim | 1S10-1105 | RURAL | 3218 | 0 | 0 | 24:00:00
168 | MAPUSA | 33 KV Anjuna | 11KV Starco | 1S15-1103 | RURAL |  | 2 | 4860 | 23:57 | Trip on OC & E/F inform HT staff test charge taken stood ok
169 | PANJIM | 33KV Corlim | 11KV New Ind.Estate | 2S01-1103 | URBAN | 327 | 0 | 0 | 24:00:00
170 | PANJIM | 33KV EDC | 11KV Patto-Plaza | 2S02-1103 | URBAN | 515 | 0 | 0 | 24:00:00
171 | PANJIM | 33KV Bambolim | 11KV Siridao | 2S05-1101 | RURAL | 1053 | 0 | 0 | 24:00:00
172 | PANJIM | 33KV Nagali hills(IT Park) | 11KV Adraar | 2S07-1101 | URBAN | 1327 | 0 | 0 | 24:00:00
173 | PANJIM | 33KV Nagali hills(IT Park) | 11KV CARANZALEM | 2S07-1102 | URBAN | 957 | 0 | 0 | 24:00:00
174 | PANJIM | 33KV Curti | 11KV Shanti Nagar | 2S10-1105 | URBAN | 4256 | 0 | 0 | 24:00:00
175 | PANJIM | 33KV Kundaim | 11KV Mardol | 2S14-1101 | RURAL | 3618 | 4 | 5160 | 23:57 | Earth fault trip,Overcurrent fault and jumper opened
176 | MARMAGAO | 110/33/11 KV Verna | 11KV IFB | 3S04-1104 | URBAN | 120 | 0 | 0 | 24:00:00
177 | MARGAO | 33KV Benaulim | 11KV Colva | 4S07-1102 | RURAL | 4699 | 0 | 0 | 24:00:00
178 | MARGAO | 33KV Velim | 11KV Dramapur | 4S10-1105 | RURAL |  | 0 | 0 | 24:00:00
179 | MARGAO | 33KV Canacona | 11KV Agonda | 4S11-1101 | RURAL | 1432 | 0 | 0 | 24:00:00
180 | MARGAO | 33KV Canacona | 11KV Gaondongri | 4S11-1104 | RURAL | 2395 | 1 | 420 | 24:00 | Incoming supply failure and load changeover.
181 | MARGAO | 33KV Pontemol | 11KV Kakoda | 4S13-1108 | URBAN | 1568 | 2 | 6780 | 23:56 | To replace failed LA, Alternate supply were given on Kakoda feeder.
182 | MARGAO | 33KV Shigao | 11KV Dhat | 4S14-1103 | RURAL | 861 | 0 | 0 | 24:00:00
183 | MARGAO | 33KV Xelpem | 11KV Ponsamol | 4S18-1102 | RURAL | 1555 | 0 | 0 | 24:00:00
184 | MAPUSA | 33KV Pernem | 11KV Nagzar | 1S01-1101 | RURAL | 3585 | 9 | 16620 | 23:51 | Tree branch fallen on line at Ozarim, Chandel. Coconut leaf fallen on line at Allorna, Bamboo stick fallen on line at Hali. Disc insulator and pin insulators faults on line Ozarim, Hali, Amai
185 | MAPUSA | 33KV Tuem | 11KV Morjim | 1S02-1104 | RURAL | 5369 | 0 | 0 | 24:00:00
186 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate II (U/G) | 1S03-1107 | URBAN |  | 2 | 6846 | 23:56 | Manually tripped , Fault Trippings
187 | MAPUSA | 33KV Mapusa | 11KV Sodiem | 1S04-1111 | RURAL | 3424 | 0 | 0 | 24:00:00
188 | MAPUSA | 33KV Nagoa | 11KV Sanqwadi | 1S07-1106 | RURAL | 1215 | 0 | 0 | 24:00:00
189 | MAPUSA | 33KV Saligao | 11KV Candolim church | 1S10-1102 | RURAL | 968 | 0 | 0 | 24:00:00
190 | MAPUSA | 33KV Saligao | 11KV Shervani Calangute | 1S10-1103 | RURAL | 2610 | 1 | 3060 | 23:58 | M/T, O/C
191 | MAPUSA | 33KV Pale | 11KV Nanus | 1S14-1101 | RURAL | 1927 | 0 | 0 | 24:00:00
192 | MAPUSA | 33KV Pale | 11KV Kotumbi | 1S14-1102 | RURAL | 667 | 0 | 0 | 24:00:00
193 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Tivaiwaddo | 1S18-1108 | RURAL |  | 0 | 0 | 24:00:00
194 | PANJIM | 33KV Corlim | 11KV Old Goa | 2S01-1102 | RURAL | 1387 | 0 | 0 | 24:00:00
195 | PANJIM | 33KV Corlim | 11KV Old Industry | 2S01-1105 | URBAN | 82 | 0 | 0 | 24:00:00
196 | PANJIM | 33KV Altinho | 11KV Circuit House | 2S04-1103 | URBAN | 743 | 0 | 0 | 24:00:00
197 | PANJIM | 33KV Bambolim | 11KV MES | 2S05-1102 | RURAL | 4 | 0 | 0 | 24:00:00
198 | PANJIM | 33KV Nagali hills(IT Park) | 11KV OITIYANT | 2S07-1103 | URBAN | 643 | 0 | 0 | 24:00:00
199 | PANJIM | 33KV Colony | 11KV Rajiv Gandhi Kala Mandir | 2S09-1106 | URBAN |  | 0 | 0 | 24:00:00
200 | PANJIM | 33KV Curti | 11KV Sarvoiverem | 2S10-1104 | RURAL | 2878 | 0 | 0 | 24:00:00
201 | MARMAGAO | 33KV Majorda | 11KV Duguem | 3S05-1105 | RURAL | 2317 | 0 | 0 | 24:00:00
202 | MARMAGAO | 33KV Majorda | 11KV Nuvem | 3S05-1106 | RURAL | 2154 | 0 | 0 | 24:00:00
203 | MARMAGAO | 33KV Bogda | ANTARTICA - Headland II | 3S06-1104 | URBAN |  | 0 | 0 | 24:00:00
204 | MARMAGAO | 33KV Bogda | MASJID | 3S06-1105 | RURAL |  | 3 | 1560 | 23:59 | 1)33KV Incomer I supply failed 2) Feeder tripped manually as a part of civil defense preparedness mock drill 3) 33KV Incomer I incoming supply failed due to LA failed in the sub station yard 4) 33KV Incomer I incoming supply failed due to 33 KV incomer cable failed, full load shifted to 33 KV incomer 2 5) 33 KV incomer supply failed due to annual shutdown taken for maintenance 6) 33KV Incomer II incoming supply failed due shutdown taken at Sancoale S/S(incomer 1 cable fault is not yet rectified) 7) 33KV Incomer I incoming supply failed
205 | MARGAO | 33KV KRC | 11KV Navelim | 4S05-1101 | RURAL | 3874 | 0 | 0 | 24:00:00
206 | MARGAO | 33KV KRC | 11KV Mandopa | 4S05-1102 | RURAL | 4104 | 7 | 7800 | 23:56 | Single phase jumper cut
207 | MARGAO | 33KV Benaulim | 11KV Betal Betim | 4S07-1103 | RURAL | 2730 | 8 | 7680 | 23:56 | 33KV Nessai-III Incoming Supply Failed
208 | MARGAO | 33KV Velim | 11KV Kumbia bhat | 4S10-1103 | RURAL | 728 | 0 | 0 | 24:00:00
209 | MARGAO | 33KV Shigao | 11KV Mollem | 4S14-1102 | RURAL | 961 | 0 | 0 | 24:00:00
210 | MAPUSA | 33KV Pernem | 11KV Torse | 1S01-1102 | RURAL | 2343 | 0 | 0 | 24:00:00
211 | MAPUSA | 33KV Mapusa | 11KV Khorlim | 1S04-1107 | URBAN | 2455 | 0 | 0 | 24:00:00
212 | MAPUSA | 33KV Porvorim | 11KV Salai | 1S09-1108 | RURAL | 1197 | 0 | 0 | 24:00:00
213 | MAPUSA | 33KV Porvorim | 11KV GURUDWARA | 1S09-1111 | URBAN |  | 0 | 0 | 24:00:00
214 | MAPUSA | 33KV Saligao | 11KV PILERNE (UG) | 1S10-1110 | RURAL |  | 0 | 0 | 24:00:00
215 | MAPUSA | 33KV Valpoi | 11KV Dabose | 1S11-1106 | RURAL |  | 2 | 26100 | 23:46 | For tree cutting / Maintenace work.
216 | MAPUSA | 33KV Sal | 11KV Ibrampur | 1S16-1102 | RURAL |  | 0 | 0 | 24:00:00
217 | PANJIM | 33KV Altinho | 11KV Tonca Miramar | 2S04-1108 | URBAN | 1682 | 0 | 0 | 24:00:00
218 | PANJIM | 33KV PILAR | 11KV Agasaim | 2S06-1102 | RURAL | 2032 | 0 | 0 | 24:00:00
219 | PANJIM | 33KV Bethora | 11KV Shiroda | 2S13-1101 | RURAL | 419 | 1 | 2880 | 23:58 | 1) planed shutdown
220 | MARMAGAO | 33KV Kadamba | 11KV Vasco church | 3S02-1102 | URBAN | 4152 | 5 | 3009.6 | 23:58 | m/t, OC/EFR.
221 | MARMAGAO | 33KV Sancoale | 11KV Vasco-II | 3S03-1106 | RURAL | 2463 | 0 | 0 | 24:00:00
222 | MARGAO | 33KV Monte Hill | 11KV GVN1 | 4S03-1102 | URBAN | 2555 | 3 | 4260 | 23:58 | Due to cable fault
223 | MARGAO | 33KV Cuncolim | 11KV IDC II | 4S09-1101 | RURAL | 118 | 1 | 840 | 24:00 | Work of insul coating was carried out on the panel.
224 | MARGAO | 33KV Poinguinim | 11KV Loliem | 4S12-1105 | RURAL | 2515 | 2 | 1380 | 23:59 | Incoming supply failure and load changeover.
225 | MAPUSA | 33KV Pernem | 11KV Keri | 1S01-1106 | RURAL | 6288 | 6 | 13440 | 23:53 | Coconut tree fallen on line at Parashte, Pin insulator fault at Kondalwada, Pernem. Tree branches fallen on line at Korgao
226 | MAPUSA | 33KV Tuem | 11KV Mandrem | 1S02-1102 | RURAL | 5315 | 5 | 4080 | 23:58 | Tripped on E/F- Conductor snapped at Atchut House, Tripped on O/C , R/Y- open jumper attended & charged.
227 | MAPUSA | 33KV Mapusa | 11KV Industry | 1S04-1101 | URBAN | 56 | 3 | 2520 | 23:59 | Change over
228 | MAPUSA | 33KV Mapusa | 11KV Karaswada | 1S04-1104 | URBAN | 1148 | 0 | 0 | 24:00:00
229 | MAPUSA | 33KV Mapusa | 11KV Parra | 1S04-1113 | RURAL | 3764 | 3 | 2520 | 23:59 | Changeover
230 | MAPUSA | 33KV Bicholim | 11KV Lamgao | 1S05-1112 | RURAL |  | 2 | 1020 | 23:59 | 33KV Changeover, Maintenace shutdown
231 | MAPUSA | 33KV Nachinola | 11KV Pomburpa | 1S06-1101 | RURAL | 1451 | 0 | 0 | 24:00:00
232 | MAPUSA | 33KV Porvorim | 11KV Malim | 1S09-1104 | RURAL | 1570 | 0 | 0 | 24:00:00
233 | PANJIM | 33KV EDC | 11KV BAL BHARTI | 2S02-1108 | URBAN |  | 0 | 0 | 24:00:00
234 | MARMAGAO | 33KV Kadamba | 11KV Waddem Lake | 3S02-1104 | URBAN | 2330 | 3 | 1440 | 23:59 | m/t, tightening of line and tree cutting done.
235 | MARMAGAO | 33KV Sancoale | 11KV Sesa Goa | 3S03-1101 | URBAN | 1484 | 0 | 0 | 24:00:00
236 | MARMAGAO | 110/33/11 KV Verna | 11KV SMARTLINK | 3S04-1109 | URBAN |  | 0 | 0 | 24:00:00
237 | MARGAO | 33KV Fatorda | 11KV Gogol | 4S02-1106 | RURAL |  | 0 | 0 | 24:00:00
238 | MARGAO | 33KV Aquem | 11KV Davorlim | 4S04-1106 | RURAL | 2293 | 0 | 0 | 24:00:00
239 | MARGAO | 33KV Nessai | 11KV Chandor | 4S06-1103 | RURAL | 2911 | 0 | 0 | 24:00:00
240 | MARGAO | 33KV Benaulim | 11KV Mobor | 4S07-1104 | RURAL | 1360 | 0 | 0 | 24:00:00
241 | MARGAO | 33KV Velim | 11KV Assolna | 4S10-1101 | RURAL | 3397 | 0 | 0 | 24:00:00
242 | MARGAO | 33KV Poinguinim | 11KV Link line | 4S12-1101 | RURAL |  | 0 | 0 | 24:00:00
243 | MARGAO | 33KV Xelpem | 11KV Dando | 4S18-1105 | RURAL | 414 | 0 | 0 | 24:00:00
244 | MAPUSA | 220/33KV Thivim | 11KV Sirsaim | 1S03-1106 | RURAL | 1888 | 0 | 0 | 24:00:00
245 | MAPUSA | 33KV Bicholim | 11KV ADVALPAL | 1S05-1105 | RURAL | 1247 | 15 | 36420 | 23:40 | Planned Shutdown UG Work, Line Faults E/F Inuslator failure, O/C Tree fallen
246 | MAPUSA | 33KV Bicholim | 11KV City | 1S05-1108 | RURAL | 3526 | 2 | 1320 | 23:59 | For 33KV Changeover, Maintenace shutdown
247 | MAPUSA | 33KV Bicholim | 11KV Kudchirem | 1S05-1111 | RURAL | 1209 | 8 | 17880 | 23:50 | Planned Shutdown, Line Faults E/F Inuslator failure, O/C Tree fallen
248 | MAPUSA | 33KV Nachinola | 11KV Aldona OH | 1S06-1102 | RURAL | 4570 | 0 | 0 | 24:00:00
249 | MAPUSA | 33KV Sanquelim | 11KV Amona | 1S08-1103 | URBAN | 3050 | 8 | 11220 | 23:54 | For maintenance and tree cutting
250 | MAPUSA | 33KV Porvorim | 11KV RND | 1S09-1103 | RURAL | 3373 | 0 | 0 | 24:00:00
251 | MAPUSA | 33KV Porvorim | 11KV Chogum | 1S09-1110 | RURAL | 3678 | 0 | 0 | 24:00:00
252 | PANJIM | 33KV Corlim | 11KV Carambolim | 2S01-1104 | RURAL | 3888 | 2 | 10539 | 23:54 | Manual tripping for erection of new transformer at Sapna Sarovar.
253 | PANJIM | 33KV Campal | 11KV Adarsh | 2S03-1105 | URBAN | 2705 | 0 | 0 | 24:00:00
254 | PANJIM | 33KV Altinho | 11KV National | 2S04-1101 | URBAN | 1276 | 0 | 0 | 24:00:00
255 | PANJIM | 33KV Altinho | 11KV Manoshanti | 2S04-1106 | URBAN |  | 0 | 0 | 24:00:00
256 | PANJIM | 33KV NIO | 11KV NIO Colony | 2S08-1105 | URBAN | 317 | 0 | 0 | 24:00:00
257 | PANJIM | 33KV Colony | 11KV Khadpabandh | 2S09-1103 | URBAN | 4107 | 0 | 0 | 24:00:00
258 | PANJIM | 33KV Curti | 11KV Curti | 2S10-1108 | URBAN |  | 0 | 0 | 24:00:00
259 | PANJIM | 33KV Kundaim | 11KV Industry II | 2S14-1106 | URBAN | 207 | 2 | 3840 | 23:58 | Shutdown declared
260 | PANJIM | 33KV Madkai | 11KV Industry II | 2S15-1105 | URBAN | 69 | 6 | 4680 | 23:57 | Shutdown declared for maintainance and jumper opened
261 | MARMAGAO | 33KV Harbour | 11KV Mangor | 3S01-1104 | URBAN | 4232 | 0 | 0 | 24:00:00
262 | MARMAGAO | 33KV Sancoale | 11KV Dabolim | 3S03-1109 | URBAN |  | 4 | 2520 | 23:59 | Feeder was manually tripped on 18/5/025 as per planned shutdown availed for entire Mormugao taluka.
263 | MARMAGAO | 110/33/11 KV Verna | 11KV Industrial | 3S04-1103 | URBAN | 114 | 0 | 0 | 24:00:00
264 | MARMAGAO | 33KV Bogda | Brahmasthal - vasco 1 | 3S06-1102 | URBAN |  | 0 | 0 | 24:00:00
265 | MARMAGAO | 33KV Bogda | HARBOUR | 3S06-1103 | URBAN |  | 0 | 0 | 24:00:00
266 | MARGAO | 33KV Raia | 11KV Loutalim | 4S01-1102 | RURAL | 2943 | 0 | 0 | 24:00:00
267 | MARGAO | 33KV Monte Hill | 11KV Adarsh | 4S03-1104 | URBAN | 1578 | 0 | 0 | 24:00:00
268 | MARGAO | 33KV Nessai | 11KV Paroda | 4S06-1102 | RURAL | 2361 | 0 | 0 | 24:00:00
269 | MARGAO | 33KV Benaulim | 11KV Varca | 4S07-1105 | RURAL | 2308 | 0 | 0 | 24:00:00
270 | MARGAO | 33KV Pontemol | 11KV Kalay | 4S13-1104 | RURAL | 177 | 1 | 600 | 24:00 | Interuptions due to unit failure and tree branch fallen.
271 | MARGAO | 220/33/11KV Xeldem | 11KV Assolda | 4S15-1104 | RURAL | 1695 | 0 | 0 | 24:00:00
272 | MARGAO | 33KV Waddem | 11KV Bhati | 4S17-1101 | RURAL | 522 | 0 | 0 | 24:00:00
273 | MAPUSA | 33KV Tuem | 11KV Ashvem Cable | 1S02-1105 | RURAL |  | 0 | 0 | 24:00:00
274 | MAPUSA | 33KV Mapusa | 11KV Anjuna | 1S04-1106 | RURAL | 4653 | 0 | 0 | 24:00:00
275 | MAPUSA | 33KV Mapusa | 11KV Assagao | 1S04-1110 | RURAL | 3620 | 10 | 13740 | 23:52 | Trip on Earth fault, Tree fallen on line near school (Banyan tree)
276 | MAPUSA | 33KV Bicholim | 11KV Ladphem | 1S05-1103 | RURAL | 2232 | 0 | 0 | 24:00:00
277 | MAPUSA | 33KV Bicholim | 11KV Narva | 1S05-1106 | RURAL | 2189 | 7 | 44640 | 23:35 | Planned Shutdown, Line Faults E/F Inuslator failure, O/C Tree fallen
278 | MAPUSA | 33KV Nachinola | 11KV Moira | 1S06-1103 | RURAL | 3008 | 0 | 0 | 24:00:00
279 | MAPUSA | 33KV Nachinola | 11KV Bastora | 1S06-1104 | RURAL | 2213 | 0 | 0 | 24:00:00
280 | MAPUSA | 33KV Sal | 11KV Sal | 1S16-1101 | RURAL |  | 0 | 0 | 24:00:00
281 | PANJIM | 33KV Corlim | 11KV Dhulapi | 2S01-1101 | RURAL | 1284 | 0 | 0 | 24:00:00
282 | PANJIM | 33KV EDC | 11KV Vidyut Bhawan | 2S02-1104 | URBAN | 735 | 0 | 0 | 24:00:00
283 | PANJIM | 33KV Altinho | 11KV Alcon | 2S04-1104 | URBAN | 1407 | 0 | 0 | 24:00:00
284 | PANJIM | 33KV Bambolim | 11KV Donapaula | 2S05-1103 | RURAL | 1904 | 0 | 0 | 24:00:00
285 | PANJIM | 33KV Curti | 11KV OPA | 2S10-1103 | RURAL | 554 | 0 | 0 | 24:00:00
286 | PANJIM | 33KV Kundaim | 11KV Marcel | 2S14-1102 | RURAL | 6565 | 0 | 0 | 24:00:00
287 | PANJIM | 33KV Madkai | 11KV Undir | 2S15-1101 | RURAL | 1773 | 6 | 4500 | 23:58 | Earth fault, and substation PT bus insulator failure
288 | MARMAGAO | 110/33/11 KV Verna | 11KV Herald | 3S04-1102 | URBAN | 70 | 2 | 6180 | 23:57 | Tripped on Earth Fault
289 | MARMAGAO | 110/33/11 KV Verna | 11KV Jordan | 3S04-1105 | URBAN | 77 | 0 | 0 | 24:00:00
290 | MARMAGAO | 33KV Majorda | 11KV Ramesh Hotel | 3S05-1101 | URBAN | 1 | 0 | 0 | 24:00:00
291 | MARGAO | 33KV Raia | 11KV Raia | 4S01-1101 | RURAL | 2613 | 1 | 360 | 24:00 | 2 Post insulator & LA punctured on 1st DT of Santemol feeder pulled 11 KV Raia feeder during fault. Occurred during thunderstorm
292 | MARGAO | 33KV Raia | 11KV Rachol | 4S01-1104 | RURAL | 1233 | 0 | 0 | 24:00:00
293 | MARGAO | 33KV Fatorda | 11KV Old market U/G | 4S02-1102 | URBAN | 4118 | 0 | 0 | 24:00:00
294 | MARGAO | 33KV Aquem | 11KV Housing Board U/G | 4S04-1102 | RURAL | 2148 | 4 | 4440 | 23:58 | I/F - due to main incomer failure
295 | MARGAO | 33KV Aquem | 11KV Malbhat | 4S04-1105 | URBAN | 1989 | 0 | 0 | 24:00:00
296 | MARGAO | 33KV Nessai | 11KV MIE | 4S06-1101 | RURAL | 373 | 0 | 0 | 24:00:00
297 | MARGAO | 33KV Carmona | 11KV XIRO | 4S08-1103 | RURAL | 1213 | 0 | 0 | 24:00:00
298 | MARGAO | 33KV Canacona | 11KV Shristhal | 4S11-1102 | RURAL | 3806 | 2 | 30060 | 23:43 | Incoming supply failure and load changeover.
299 | MARGAO | 33KV Canacona | 11KV Kindlem | 4S11-1103 | RURAL |  | 0 | 0 | 24:00:00
300 | MARGAO | 33KV Pontemol | 11KV Town 2 | 4S13-1106 | URBAN | 1264 | 0 | 0 | 24:00:00
301 | MARGAO | 33KV Pontemol | 11KV HODAR | 4S13-1109 | RURAL |  | 1 | 600 | 24:00 | To check red hot on 11KV Bay
302 | MARGAO | 33KV Xelpem | 11KV Barazan | 4S18-1103 | RURAL | 1262 | 0 | 0 | 24:00:00
303 | MAPUSA | 33KV Pernem | 11KV City | 1S01-1103 | RURAL | 1464 | 5 | 7620 | 23:56 | Dry tree branches fallen on line in municipality area. Post insulator faults on DTC.
304 | MAPUSA | 220/33KV Thivim | 11KV Industrial Estate | 1S03-1101 | URBAN |  | 1 | 5520 | 23:57 | Trip on Earth fault, Nothing found on line
305 | MAPUSA | 33KV Nagoa | 11KV Calangute | 1S07-1101 | RURAL | 2986 | 7 | 20660.4 | 23:49 | Cable Foult
306 | MAPUSA | 33KV Porvorim | 11KV Sangolda | 1S09-1105 | RURAL | 2650 | 2 | 1080 | 23:59 | E/f. Tree branch fall on line
307 | MAPUSA | 33KV Saligao | 11KV Gaurawaddo | 1S10-1109 | URBAN |  | 7 | 151320 | 22:36 | M/T
308 | MAPUSA | 33KV Valpoi | 11KV City New | 1S11-1105 | RURAL | 2806 | 0 | 0 | 24:00:00
309 | MAPUSA | 33KV Sal | 11KV Kasarpal | 1S16-1103 | RURAL |  | 1 | 540 | 24:00 | Planned Shutdown
310 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Mark Memorial | 1S18-1105 | URBAN |  | 0 | 0 | 24:00:00
311 | PANJIM | 33KV Campal | 11KV St. Inez | 2S03-1107 | URBAN |  | 0 | 0 | 24:00:00
312 | PANJIM | 33KV Altinho | 11KV Cabo | 2S04-1112 | URBAN | 3821 | 0 | 0 | 24:00:00
313 | PANJIM | 33KV PILAR | 11KV Batim | 2S06-1103 | RURAL | 4199 | 3 | 2160 | 23:59 | Load shedding imposed by 110/33 KV Kadamba Plateau substation on account of Planned shutdown arranged by 220 KV Tivim Substation on 10/5/2025. 11 KV Feeders were manually tripped on rotational basis from 9:30 am to 4:00 pm.
314 | PANJIM | 33KV NIO | 11KV NIO | 2S08-1103 | URBAN | 575 | 0 | 0 | 24:00:00
315 | PANJIM | 33KV Colony | 11KV Bazaar | 2S09-1101 | URBAN | 2570 | 0 | 0 | 24:00:00
316 | PANJIM | 33KV Bethora | 11KV Industrial | 2S13-1104 | URBAN | 246 | 0 | 0 | 24:00:00
317 | PANJIM | 33KV Kundaim | 11KV Kundaim | 2S14-1104 | RURAL | 1252 | 0 | 0 | 24:00:00
318 | MARMAGAO | 33KV Kadamba | 11KV Vasco city | 3S02-1103 | URBAN | 1656 | 3 | 1440 | 23:59 | m/t, jumper cut, touching the channel attended near Vasco church.
319 | MARMAGAO | 33KV Sancoale | 11KV Vasco-I | 3S03-1103 | URBAN | 2369 | 0 | 0 | 24:00:00
320 | MARMAGAO | 110/33/11 KV Verna | 11KV Oxynitro | 3S04-1110 | RURAL |  | 0 | 0 | 24:00:00
321 | MARGAO | 33KV Fatorda | 11KV Fatorda | 4S02-1105 | URBAN | 3056 | 0 | 0 | 24:00:00
322 | MARGAO | 33KV Monte Hill | 11KV GVN2 | 4S03-1101 | URBAN |  | 0 | 0 | 24:00:00
323 | MARGAO | 33KV Cuncolim | 11KV IDC I | 4S09-1102 | RURAL | 61 | 0 | 0 | 24:00:00
324 | MARGAO | 33KV Velim | 11KV Betul | 4S10-1102 | RURAL | 1932 | 0 | 0 | 24:00:00
325 | MARGAO | 33KV Poinguinim | 11KV Marli Tirval | 4S12-1102 | RURAL | 889 | 1 | 4620 | 23:57 | Pin insulator fault, disc insulator fault,Tree branch fallen on line and jumper cut, incoming supply failure.
326 | MARGAO | 33KV Pontemol | 11KV Town 1 | 4S13-1101 | URBAN | 4338 | 0 | 0 | 24:00:00
327 | MARGAO | 33KV Rivona | 11KV Maina | 4S16-1101 | RURAL | 726 | 10 | 26340 | 23:45 | Due to frequent failure of AB cable termination kit and planned shutdown taken for tree cutting
328 | MAPUSA | 33KV Nagoa | 11KV Baga | 1S07-1107 | RURAL | 2843 | 0 | 0 | 24:00:00
329 | MAPUSA | 33KV Porvorim | 11KV Soccorro | 1S09-1101 | RURAL | 2406 | 0 | 0 | 24:00:00
330 | MAPUSA | 33KV Saligao | 11KV Industry O/H | 1S10-1106 | URBAN | 386 | 0 | 0 | 24:00:00
331 | MAPUSA | 33KV Saligao | 11KV Nerul | 1S10-1108 | RURAL | 3108 | 5 | 8760 | 23:55 | M/T and line snapping
332 | MAPUSA | 220/33KV Amona | 11 KV Pissurlem IDC | 1S13-1104 | RURAL |  | 0 | 0 | 24:00:00
333 | MAPUSA | 33/11 KV GIS CALANGUTE | 11KV Shivam | 1S18-1104 | RURAL |  | 0 | 0 | 24:00:00
334 | PANJIM | 33KV Corlim | 11KV Molar | 2S01-1106 | RURAL | 1766 | 1 | 38580 | 23:39 | Manual tripping to attend jumper in Sub Station yard.
335 | PANJIM | 33KV Campal | 11KV City | 2S03-1103 | RURAL | 596 | 0 | 0 | 24:00:00
336 | PANJIM | 33KV Nagali hills(IT Park) | 11KV STATUS | 2S07-1104 | URBAN | 887 | 0 | 0 | 24:00:00
337 | PANJIM | 33KV Colony | 11KV Curti | 2S09-1105 | URBAN |  | 0 | 0 | 24:00:00
338 | PANJIM | 33KV Dharbandora | 11KV Dharbandora | 2S11-1104 | RURAL | 1826 | 7 | 4980 | 23:57 | 1) OCR tree branches fallen on line remove and charge at Petkem 2) OCR open Dhatfarm AB switch and line charge holding 3) OCR remove tree branches fallen on line at Udalshe and than close Dongarwada,Dhatfarm tapping AB switch charge ok ( Talsai tapping close by without triping)
339 | MARMAGAO | 33KV Sancoale | 11KV College | 3S03-1107 | RURAL | 1168 | 0 | 0 | 24:00:00
340 | MARGAO | 33KV Benaulim | 11KV Colva Exp | 4S07-1107 | URBAN |  | 0 | 0 | 24:00:00
341 | MARGAO | 220/33/11KV Xeldem | 11KV Rivona | 4S15-1102 | RURAL | 2528 | 1 | 780 | 24:00 | (1) On 03/05/2025 (00:23 min) - feeder tripped on o/c. Tree branch fallen on line, charged on removing branch. OK (2) On 17/05/2025 (01:42 hrs) - Feeder M/T for tree cutting. charged OK. (3) On 20/05/2025 (00:16 min) - feeder tripped on o/c and E/F. Tilamol A/B switch opened and charged OK. (4) On 20/05/2025 (00:24 min) - Feeder M/T for closing Zambaulim A/B switch. charged OK. (5) On 22/05/2025 (00:25 min) - Feeder tripped on E/F and O/C. Tilamol A/B switch opened, feeder charged OK. (6) On 22/05/2025 (00:53 min) - Feeder tripped on E/F and O/C. Jumper opened at Xeldem outgoing bay. Attended and charged OK. (7) On 22/05/2025 (00:30 min) -Feeder tripped on E/F and O/C. Tree fallen on line, cleared and charged OK. (8) On 23/05/2025 (00:17 min) - Feeder M/T for closing Zambaulim A/B switch. Charged OK. (9) On 30/05/2025 (00:14 min) - Feeder tripped on E/F and O/C. Tree branch fall on line, cleared and charged OK.
342 | MARGAO | 33KV Rivona | 11KV Colomba | 4S16-1103 | RURAL | 316 | 1 | 13560 | 23:52 | Due to frequent failure of AB cable termination kit and planned shutdown taken for tree cutting
343 | MARGAO | 33KV Xelpem | 11KV Sanguem | 4S18-1101 | URBAN | 2566 | 2 | 9120 | 23:55 | Shutdown taken for new LT line stringing work,DTC Renovation work, Planned shutdown for tree cutting and routine maintenance of HT/LT line